## Summary
ETC Lighting Controls Survey
Levels B2-06
Surveyed 2026-10-07 to 2026-10-09
THIS SHEET IS NOT A SUBSTITUTE FOR THE SUBMITTAL DRAWINGS! PLEASE REFER TO SUBMITTALS BEFORE ACTING ON ANY NOTES IN THIS SHEET!
Device status by floor
Floor | Surveyed | Updated | Installed, untested | Issue | Not installed | No access | Complete | Total
B2 | 2026-10-09 |  | 1 | 3 | 1 | 0 | 0 | 5
B1 | 2026-10-08 |  | 6 | 9 | 12 | 12 | 0 | 39
01 | 2026-10-07 | 2026-10-08 | 6 | 7 | 22 | 1 | 0 | 36
02 | 2026-10-07 | 2026-10-08 | 26 | 4 | 15 | 0 | 0 | 45
03 | 2026-10-07 | 2026-10-08 | 16 | 9 | 11 | 0 | 0 | 36
04 | 2026-10-07 | 2026-10-08 | 2 | 15 | 14 | 0 | 0 | 31
06 | 2026-10-07 |  | 12 | 0 | 2 | 0 | 0 | 14
06M | 2026-10-07 |  | 1 | 3 | 0 | 0 | 0 | 4
Total |  |  | 70 | 50 | 77 | 13 | 0 | 210
Outstanding items by floor
Floor | Open | In progress | Closed | Total
B2 | 9 | 0 | 0 | 9
B1 | 28 | 0 | 0 | 28
01 | 46 | 1 | 6 | 53
02 | 27 | 0 | 5 | 32
03 | 29 | 0 | 2 | 31
04 | 41 | 0 | 3 | 44
06 | 3 | 0 | 0 | 3
06M | 15 | 0 | 0 | 15
Total | 198 | 1 | 16 | 215
Outstanding items by owner
Owner | Open | In progress | Closed | Total
EC | 168 | 0 | 1 | 169
ETC | 9 | 0 | 15 | 24
EC/ETC | 21 | 1 | 0 | 22
Total | 198 | 1 | 16 | 215
Missing parts by floor
Floor | Needed | Ordered | On site | Installed | Total
B2 | 3 | 0 | 0 | 0 | 3
B1 | 8 | 0 | 0 | 0 | 8
01 | 17 | 0 | 1 | 2 | 20
02 | 10 | 0 | 0 | 0 | 10
03 | 16 | 0 | 0 | 0 | 16
04 | 12 | 0 | 1 | 0 | 13
06 | 2 | 0 | 0 | 0 | 2
06M | 13 | 0 | 0 | 0 | 13
Total | 81 | 0 | 2 | 2 | 85

## Devices
Devices
Levels B2-06
Level | ID | Category | Device | Type | Room / Location | Drawing Position | Status | Notes | Photo | Floor Order
B2 | B2-01 | Relay panel | CTB2LCPB | Echo ERP-FT-241P (24x20 relays) | Elec XXB2-2E02 | Grid B-C / 9-8 | Issue | 0-10V not run. DMX run, not terminated. Network and 4x Unison wires land in ERP; need to be run down to the P-NSPS-D. | 1 | 1
B2 | B2-02 | EBDK | EBDK | Emergency Bypass Detection Kit (CTB2LCPB) | Elec XXB2-2E02 | Grid C / 9-8 | Installed, untested |  |  | 1
B2 | B2-03 | NSPS | P-NSPS-D-KIT | Paradigm network station power supply | Elec XXB2-2E02 | Grid B-C / 9-8 | Issue | Missing 48V jumper from power supply to NSPS. 120V not run to NSPS power supply. | 2 | 1
B2 | B2-S1 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby B XXB2-C003, east | Grid C / 9.5-9 | Issue | Missing cover. | 3 | 1
B2 | B2-D1 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby B XXB2-C003 | Grid B-C / 9.5-9 | Not installed | Not Installed - box present. | 4 | 1
B1 | B1-01 | Relay panel | CTB1LCPB | Echo ERP-FT-241P (24x20 relays) | Elec WTB1-1E01; moved from Elec XXB1-2E02 | WT Grid C.-D. / 4.-3 | Issue | Missing ERP-RTO jumper. Panel loads not landed. 0-10V not run. Both DMX run, not terminated. | 1 | 2
B1 | B1-02 | EBDK | EBDK | Emergency Bypass Detection Kit (CTB1LCPB) | Elec WTB1-1E01; moved from Elec XXB1-2E02 | WT Grid C.-D. / 4.-3 | Issue | No sense feed. | 1 | 2
B1 | B1-S1 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby B XXB1-C003, east | Grid C / 9.5-9 | Not installed | Not Installed - no box. |  | 2
B1 | B1-S2 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XXB1-C007 at Stair F XXB1-3S02 | Grid A-B / 7 | Not installed | Not Installed - box present with wire. | 4 | 2
B1 | B1-S3 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XXB1-C005, north | Grid E-F / 6.6-6.4 | Issue | Missing cover. | 9, 10 | 2
B1 | B1-S4 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XXB1-C005, south | Grid E-F / 6.4-5.5 | Issue | Missing cover. | 11 | 2
B1 | B1-S5 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby C XXB1-C002 | Grid F / 6.4-5.5 | Issue | Missing cover. |  | 2
B1 | B1-S6 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XXB1-C004 at IDF XXB1-1I05 | Grid East of G / 6.6 | Issue | Missing cover. |  | 2
B1 | B1-S7 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XXB1-C008, west | Grid East of G / 6.6-6.4 | Issue | Missing cover. |  | 2
B1 | B1-S8 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XXB1-C008, east at Gas Cyldr XXB1-1002 | Grid East of G / 6.6 | Issue | Missing cover. |  | 2
B1 | B1-S9 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor at Drinking Fountain XXB1-1004 | Grid East of G / 5.5 | Issue | Missing cover. |  | 2
B1 | B1-S10 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor WTB1-C016, north | WT Grid C.-D. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-S11 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor WTB1-C011, west | WT Grid D.-E. / 6. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-S12 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor WTB1-C012 | WT Grid E.-F. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-S13 | Station | PI1002 | Paradigm Inspire 2-button station | Fire Protection Closet WTB1-2008 | WT Grid H.-J. / 6. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-S14 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor WTB1-C016 at Elec WTB1-1E01 | WT Grid C.-D. / 3.-2. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-S15 | Station | PI1002 | Paradigm Inspire 2-button station | Passage WTB1-C017 at Elec WTB1-1E01 | WT Grid C.-D. / 3.-2. | Installed, untested |  |  | 2
B1 | B1-S16 | Station | PI1002 | Paradigm Inspire 2-button station | EVS Check-In Alcove WTB1-2044 | WT Grid A.-B. / 4.-3. | Installed, untested |  |  | 2
B1 | B1-D1 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C009 at Water Meter XXB1-3WM01 | Grid B-C / 13-12.8 | Not installed | Not Installed - box present. | 2 | 2
B1 | B1-D2 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C009 at Fan Room XXB1-2F01 | Grid C-D / 13-12.8 | Not installed | Not Installed - box present. | 3 | 2
B1 | B1-D3 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Elevator Lobby B XXB1-C003, west | Grid B / 9.5-9 | Not installed | Not Installed - no box. |  | 2
B1 | B1-D4 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby B XXB1-C003 | Grid B-C / 9.5-9 | Not installed | Not Installed - no box. |  | 2
B1 | B1-D5 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C007, north | Grid A-B / 6.8 | Not installed | Not Installed - box present. | 5 | 2
B1 | B1-D6 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C007, south at Confident Waste XXB1-3017 | Grid A-B / 5.5 | Not installed | Not Installed - box present. | 6 | 2
B1 | B1-D7 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C006 at Cart Wash XXB1-3007 | Grid C-D / 5.5 | Not installed | Not Installed - box present. | 7 | 2
B1 | B1-D8 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C006 at Trash Compactor XXB1-2TC01 | Grid D-E / 5.5 | Not installed | Not Installed - box present. | 8 | 2
B1 | B1-D9 | Sensor | P-DOC-W | Paradigm wall occupancy sensor | Corridor XXB1-C005 at Elevator CT-C1 | Grid E-F / 5.5 | Installed, untested |  |  | 2
B1 | B1-D10 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XXB1-C005 | Grid E-F / 6.6-6.4 | Installed, untested |  |  | 2
B1 | B1-D11 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby C XXB1-C002 | Grid F / 6.4-5.5 | Installed, untested |  |  | 2
B1 | B1-D12 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XXB1-C004 at IDF XXB1-1I05 | Grid East of G / 6.6-6.4 | Installed, untested |  |  | 2
B1 | B1-D13 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XXB1-C008, west | Grid East of G / 6.6-6.4 | Not installed | Not Installed. | 12 | 2
B1 | B1-D14 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XXB1-C008, east at Gas Cyldr XXB1-1002 | Grid East of G / 6.6-6.4 | Not installed | Not Installed. |  | 2
B1 | B1-D15 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C010 at Corridor WTB1-C016 | WT Grid C.-D. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-D16 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C011, west | WT Grid D.-E. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-D17 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C011 at Corridor WTB1-C012 | WT Grid E.-F. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-D18 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C011, east | WT Grid G.-H. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-D19 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C016, north | WT Grid C.-D. / 6.-5. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-D20 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C016 | WT Grid C.-D. / 5.-4. | No access | Blocked by Walter Tower barricade. |  | 2
B1 | B1-D21 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor WTB1-C016 at Elec WTB1-1E01 | WT Grid C.-D. / 4.-3. | No access | Blocked by Walter Tower barricade. |  | 2
01 | 01-01 | Relay panel | CT01LCPB | Echo ERP-FT-481P (48x20 relays) | Elec XX01-1E02 | Grid F-G / 8 | Issue | Missing 1x ERP-RTO jumper, 1x ERP-FT-LVD (0-10V card). 0-10V not landed. | 14 | 3
01 | 01-02 | EBDK | EBDK | Emergency Bypass Detection Kit (CT01LCPB) | Elec XX01-1E02 | Grid F-G / 8-7.5 | Installed, untested |  |  | 3
01 | 01-03 | Relay panel | CT01LCPA | Echo ERP-FT-481P (48x20 relays) | Elec XX01-1E01 | Grid E / 7.5 | Issue | Missing 1x ERP-FT-LVD (0-10V card). 0-10V run, not terminated | 15 | 3
01 | 01-04 | EBDK | EBDK | Emergency Bypass Detection Kit (CT01LCPA) | Elec XX01-1E01 | Grid E-F / 7.5 | Installed, untested |  | 15 | 3
01 | 01-05 | Equipment rack | Equipment Rack 18U | Unison ERn4-RM rack (2x P-ACP, 2x P-SPM-E, Mosaic MSCX-10, switch, UPS) | Elec WT01-1E02 | Grid F-G / south of 5; moved | Issue | Missing 1x 1U brush panel, 1x SGM1612 & 1x SGN1021. Run to rack: 3 DMX, 2 net, 1 ground, 1 fiber; 120V run and terminated but box not secured. | 12,13 | 3
01 | 01-06 | Touchscreen | P-TS7-E | Paradigm 7in touchscreen | Info Desk WT01-1046 | Grid East of H / 10-9.5 | Not installed | Not Installed. |  | 3
01 | 01-07 | Foundry panel | UFMP4 | Foundry 4-circuit panel | Vest WT01-1044 | Grid East of H / 10 | Not installed | Not Installed. |  | 3
01 | 01-08 | Foundry panel | UFMP4 | Foundry 4-circuit panel | BH OBS RM 47 WT01-2027 | Grid East of H / 9.5-9 | Not installed | Not Installed. |  | 3
01 | 01-09 | Foundry panel | UFMP4 | Foundry 4-circuit panel | BH OBS RM 48 WT01-2010 | Grid East of H / 9 | Not installed | Not Installed. |  | 3
01 | 01-10 | Foundry panel | UFMP4 | Foundry 4-circuit panel | BH OBS RM 49 WT01-2008 | Grid East of H / 9-8 | Not installed | Not Installed; unit mounted above ceiling, but not installed otherwise. | 5 | 3
01 | 01-11 | Foundry panel | UFMP4 | Foundry 4-circuit panel | BH OBS RM 50 WT01-2006 | Grid East of H / 9-8 | Not installed | Not Installed; unit mounted above ceiling, but not installed otherwise. |  | 3
01 | 01-12 | Foundry panel | UFMP4 | Foundry 4-circuit panel | BH OBS RM 51 WT01-2004 | Grid East of H / 8 | Not installed | Not Installed; unit mounted above ceiling, but not installed otherwise. |  | 3
01 | 01-13 | Foundry panel | UFMP4 | Foundry 4-circuit panel | BH OBS RM 52 WT01-2002 | Grid East of H / 8-7.5 | Not installed | Not Installed; unit mounted above ceiling, but not installed otherwise. |  | 3
01 | 01-S1 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | NS XX01-2017 | Grid D-E / 10 | Installed, untested |  |  | 3
01 | 01-S2 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX01-C018 at Tlt. Pub XX01-2014 | Grid C-D / 10-9.5 | Issue | Wire nuts. |  | 3
01 | 01-S3 | Station | PI1002 | Paradigm Inspire 2-button station | Alc. Stretcher XX01-2022 / Corridor XX01-C016 | Grid C-D / 9.5-9 | Installed, untested |  |  | 3
01 | 01-S4 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Discharge XX01-2106 | Grid E-F / 10-9.5 | Issue | Wire nuts. |  | 3
01 | 01-S5 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Info Desk WT01-1046 / WC Storage WT01-1045 | Grid East of H / 10-9.5 | Not installed | Not Installed - no box; wire out of stone wall. | 9 | 3
01 | 01-S6 | Station | PI1002 | Paradigm Inspire 2-button station | Humidifier Closet WT01-2033 | Grid East of H / 10-9.5 | No access | Blocked by Walter Tower barricade. |  | 3
01 | 01-S7 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | BH OBS RM 47 WT01-2027 | Grid East of H / 9.5-9 | Not installed | Not Installed. |  | 3
01 | 01-S8 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Passageway WT01-C022 at BH OBS RM 48 | Grid East of H / 9 | Not installed | Not Installed; 3-gang box for 1-gang switch. | 6 | 3
01 | 01-S9 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Passageway WT01-C022 at BH OBS RM 49 | Grid East of H / 9-8 | Not installed | Not Installed; 3-gang box for 1-gang switch. | 6 | 3
01 | 01-S10 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Passageway WT01-C022 at BH OBS RM 50 | Grid East of H / 9-8 | Not installed | Not Installed; 3-gang box for 1-gang switch. | 6 | 3
01 | 01-S11 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Passageway WT01-C022 at BH OBS RM 51 | Grid East of H / 8 | Not installed | Not Installed; 3-gang box for 1-gang switch. | 6 | 3
01 | 01-S12 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Passageway WT01-C022 at BH OBS RM 52 | Grid East of H / 8-7.5 | Not installed | Not Installed; 3-gang box for 1-gang switch. | 6 | 3
01 | 01-S13 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | ALC. HW WT01-C024A | Grid East of H / 9-8 | Not installed | Not Installed - box present. | 4 | 3
01 | 01-S14 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Passageway WT01-C023 west | Grid East of H / 9-8 | Not installed | Not Installed - box present. | 7 | 3
01 | 01-S15 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Hydra XX01-3137 | Grid D-E / 9-8 | Issue | Wire nuts. | 1 | 3
01 | 01-S16 | Station | PI1004 | Paradigm Inspire 4-button station | Corridor XX01-C015 | Grid E-F / 9-8 | Not installed | Not Installed - blank plate on box. | 3 | 3
01 | 01-S17 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Exam Rm 11 XX01-3111 | Grid D-E / 6.8 | Installed, untested |  |  | 3
01 | 01-S18 | Station | PI1004 | Paradigm Inspire 4-button station | SLD HLD WT01-2001 | Grid East of H / 6.6 | Not installed | Not installed, box installed, wire present, no ground. | 11 | 3
01 | 01-S19 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX01-C004 | Grid F / 6.4 | Issue | Wire nuts. | 2 | 3
01 | 01-S20 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | NS WT01-2101 | Grid H / 6.4 | Not installed | Not installed, box installed, wire present, no ground. | 10 | 3
01 | 01-S21 | Station | PI1002 | Paradigm Inspire 2-button station | Passage XX01-C005A / Tlt. Pat XX01-3116T | Grid D / 5.2 | Installed, untested |  |  | 3
01 | 01-S22 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Tlt. Pat Stf WT01-2161 / ALC. HW WT01-C032B | Grid East of H / south of 5 | Not installed | Not Installed - box present. | 8 | 3
01 | 01-D1 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby C XX01-C002 | Grid F / 5.2 | Not installed | Not Installed. |  | 3
02 | 02-01 | Relay panel | CT02LCPA | Echo ERP-FT-241P (24x20 relays) | Elec XX02-1E01 | Grid E / 7.5 | Issue | 0-10V run not terminated, one DMX run not terminated, one DMX missing (unknown which) | 6 | 4
02 | 02-02 | EBDK | EBDK | Emergency Bypass Detection Kit (CT02LCPA) | Elec XX02-1E01 | Grid E-F / 7.5 | Issue | No sense feed. | 6 | 4
02 | 02-03 | NSPS | P-NSPS-D-KIT | Paradigm network station power supply | Elec XX02-1E01 | Grid E / 7.5 | Not installed | Not Installed. No Unison wire in Elec XX02-1E01. |  | 4
02 | 02-04 | Relay panel | CT02LCPB | Echo ERP-FT-241P (24x20 relays) | Elec XX02-1E02 | Grid E-F / 8-7.5 | Issue | 0-10V not run. 2 DMX runs to terminate; 1 net run from lvl 1 for what? | 1,5 | 4
02 | 02-05 | EBDK | EBDK | Emergency Bypass Detection Kit (CT02LCPB) | Elec XX02-1E02 | Grid F / 8-7.5 | Installed, untested |  | 5 | 4
02 | 02-06 | Foundry panel | UFMP4 | Foundry 4-circuit panel | Elec XX02-1E02 | Grid F / 8-7.5 | Not installed | Not Installed. |  | 4
02 | 02-S1 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor at Pre-Action XX02-2P01 | Grid C / 9.5-9; west end | Not installed | Not Installed. |  | 4
02 | 02-S2 | Station | PI1002 | Paradigm Inspire 2-button station | Reception XX02-2009 | Grid C-D / 9 | Issue | Stuck buttons. |  | 4
02 | 02-S3 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX02-C008 | Grid C-D / 9; south of Pre-Action | Installed, untested |  |  | 4
02 | 02-S4 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor at Tlt. Pub (M) XX02-1008 | Grid F / 9 | Installed, untested |  |  | 4
02 | 02-S5 | Station | PI1002 | Paradigm Inspire 2-button station | Central Supply WT02-2033 | Grid East of H / 9-8; west wall | Not installed | Not Installed. |  | 4
02 | 02-S6 | Station | PI1002 | Paradigm Inspire 2-button station | Central Supply WT02-2033 | Grid East of H / 9-8; east wall | Installed, untested |  |  | 4
02 | 02-S7 | Station | PI1002 | Paradigm Inspire 2-button station | Central Supply WT02-2033 | Grid East of H / 8-7.5; south | Installed, untested |  |  | 4
02 | 02-S8 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX02-C005 at IDF XX02-2I01 | Grid D-E / 8-7.5 | Installed, untested |  |  | 4
02 | 02-S9 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor at Tlt. Stf XX02-1020 / Elec XX02-1E01 door | Grid E-F / 7.5 | Installed, untested |  | 2 | 4
02 | 02-S10 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX02-C007 at Med Gas XX02-3018 | Grid A-B / 7.5 | Installed, untested |  |  | 4
02 | 02-S11 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby A XX02-C001 | Grid G / 7.5-7 | Not installed | Not installed, no box | 4 | 4
02 | 02-S12 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Seating XX02-C016, Stair C side | Grid East of H / 6.8 | Not installed | Not Installed. |  | 4
02 | 02-S13 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX02-C004 | Grid F-G / 6.6-6.4 | Not installed | Not Installed. |  | 4
02 | 02-S14 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby C XX02-C002 | Grid F / 6.4 | Not installed | Not Installed. |  | 4
02 | 02-S15 | Station | PI1002 | Paradigm Inspire 2-button station | East corridor south of Seating XX02-C016 | Grid East of H / 5 | Not installed | Not installed, no box |  | 4
02 | 02-D1 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C011 at Off. Med Dir XX02-2024 | Grid C-D / 10.5-10 | Not installed | Not Installed. |  | 4
02 | 02-D2 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C011, east | Grid D / 10.5-10 | Installed, untested |  |  | 4
02 | 02-D3 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor at Off. PAS Mgr XX02-2016 | Grid D-E / 10 | Installed, untested |  |  | 4
02 | 02-D4 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C010 | Grid C-D / 10-9.5 | Not installed | Not Installed; installed sensor at location appears to be a Wattstopper, confirm. | 3 | 4
02 | 02-D5 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C009 | Grid D-E / 9.5-9 | Installed, untested |  |  | 4
02 | 02-D6 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C012 | Grid D-E / 9.5-9 | Installed, untested |  |  | 4
02 | 02-D7 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor at Pre-Action XX02-2P01 | Grid C-D / 9.5-9 | Installed, untested |  |  | 4
02 | 02-D8 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C008, north | Grid C-D / 9-8 | Installed, untested |  |  | 4
02 | 02-D9 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor at Off. Shrd XX02-2012 | Grid D-E / 9-8 | Installed, untested |  |  | 4
02 | 02-D10 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C008 at Stor. Stretcher XX02-3007 | Grid C-D / 8 | Not installed | Not Installed. |  | 4
02 | 02-D11 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, west | Grid East of H / 9-8 | Not installed | Not Installed. |  | 4
02 | 02-D12 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, north-west | Grid East of H / 9-8 | Installed, untested |  |  | 4
02 | 02-D13 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, north-centre | Grid East of H / 9-8 | Installed, untested |  |  | 4
02 | 02-D14 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, north-east | Grid East of H / 9-8 | Installed, untested |  |  | 4
02 | 02-D15 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, south-west | Grid East of H / 8-7.5 | Installed, untested |  |  | 4
02 | 02-D16 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, south-centre | Grid East of H / 8-7.5 | Installed, untested |  |  | 4
02 | 02-D17 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Central Supply WT02-2033, south-east | Grid East of H / 8-7.5 | Installed, untested |  |  | 4
02 | 02-D18 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C007 at MDF | Grid A-B / 8-7.5 | Installed, untested |  |  | 4
02 | 02-D19 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C005 at Elec XX02-2E01 | Grid C-D / 8-7.5 | Installed, untested |  |  | 4
02 | 02-D20 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C005 at IDF | Grid D-E / 8-7.5 | Installed, untested |  |  | 4
02 | 02-D21 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C006, east | Grid C-D / 7.5 | Installed, untested |  |  | 4
02 | 02-D22 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C006, west | Grid B-C / 7.5-7 | Installed, untested |  |  | 4
02 | 02-D23 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX02-C004 | Grid F / 6.6-6.4 | Not installed | Not Installed. |  | 4
02 | 02-D24 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby C XX02-C002 | Grid F / 5.2 | Not installed | Not Installed. |  | 4
03 | 03-01 | Relay panel | CT03LCPA | Echo ERP-FT-241P (24x20 relays) | Elec XX03-1E01 | Grid E / 7-6.8 | Issue | Need new I/O card. 0-10V not landed. Both DMX run, not terminated. 2 network runs, purpose unknown. | 1, 2 | 5
03 | 03-02 | EBDK | EBDK | Emergency Bypass Detection Kit (CT03LCPA) | Elec XX03-1E01 | Grid E / 7-6.8 | Installed, untested |  | 2 | 5
03 | 03-03 | Relay panel | CT03LCPB | Echo ERP-FT-241P (24x20 relays) | Elec XX03-1E04 | Grid F-G / 9.5 | Issue | 0-10V not landed. 3 DMX run into relay panel, not terminated. | 3, 4 | 5
03 | 03-04 | EBDK | EBDK | Emergency Bypass Detection Kit (CT03LCPB) | Elec XX03-1E04 | Grid F-G / 9.5 | Installed, untested |  |  | 5
03 | 03-05 | NSPS | P-NSPS-D-KIT | Paradigm network station power supply | Elec XX03-1E04 | Grid F-G / 9.5; moved from Elec XX03-1E01 | Issue | 120V is run, needs landing into Power Supply |  | 5
03 | 03-06 | Foundry panel | UFMP4 | Foundry 4-circuit panel | Semi-Restr Corridor XX03-C028 | Grid East of H / 11-10.5; moved from OR (Stat) Lab XX03-1108 | Issue | DMX run, not terminated; need DMX term kit. Missing one DMX cable, which is missing? | 15 | 5
03 | 03-07 | Foundry panel | UFMP4 | Foundry 4-circuit panel | Semi-Restr Corridor XX03-C028 | Grid East of H / 10.5; moved from Frozen Section XX03-1106 area | Issue | DMX run, not terminated; need DMX term kit. Missing one DMX cable, which is missing? | 15 | 5
03 | 03-S1 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor at Stair A XX03-2S01 | Grid C-D / 13; at stair door | Installed, untested |  |  | 5
03 | 03-S2 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor at Med Gas Btl Stor XX03-2047 | Grid E / 12-11 | Installed, untested |  |  | 5
03 | 03-S3 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor at Off. OR Mgr XX03-1048 | Grid F / 11-10.5 | Installed, untested |  |  | 5
03 | 03-S4 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Semi-Restr Corridor XX03-C028 | Grid East of H / 11-10.5; west wall north of Frozen Section | Issue | Missing cover. | 5 | 5
03 | 03-S5 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Semi-Restr Corridor XX03-C028 | Grid East of H / 10.5; at Frozen Section XX03-1106 door | Installed, untested |  | 6 | 5
03 | 03-S6 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | ALC. Stretcher XX03-2094 | Grid A / 10.5-10 | Issue | Trim cut, broken; needs to be replaced. | 7, 8 | 5
03 | 03-S7 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor at Lng. Anes XX03-2032 / OR Ctrl Station XX03-2028 | Grid D-E / 10-9.5 | Installed, untested |  |  | 5
03 | 03-S8 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor XX03-C014A | Grid East of H / 8-7.5; at Off XX03-1104 | Not installed | Not Installed - box present. | 9 | 5
03 | 03-S9 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Reception / Info Desk XX03-2102 | Grid East of H / 7.5-7 | Issue | Missing cover. | 10 | 5
03 | 03-S10 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | ALC. HW XX03-3109 | Grid C-D / 6.8 | Installed, untested |  | 11 | 5
03 | 03-S11 | Station | PI1002 | Paradigm Inspire 2-button station | Semi-Restr Corridor XX03-C028 | Grid H / 12-11; north end | Not installed | Not Installed. |  | 5
03 | 03-S12 | Station | PI1002 | Paradigm Inspire 2-button station | Semi-Restr Corridor XX03-C028 | Grid H / 10.5; at Frozen Section door | Not installed | Not Installed. |  | 5
03 | 03-S13 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby B XX03-C003 | Grid C / 9.5-9 | Not installed | Not Installed - box present. | 12 | 5
03 | 03-S14 | Station | PI1002 | Paradigm Inspire 2-button station | ALC XX03-3006 / Lng. Stf XX03-3008 | Grid A-B / 8-7.5 | Installed, untested |  |  | 5
03 | 03-S15 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX03-C014 | Grid G / 8-7.5; north of Elevator CT-A5 | Not installed | Not Installed - box present. | 16 | 5
03 | 03-S16 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX03-C014 | Grid G / 7.5-7; south of Elevator CT-A5 | Not installed | Not Installed - box present. | 17 | 5
03 | 03-S17 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX03-C004A | Grid E-F / 6.6 | Installed, untested |  |  | 5
03 | 03-S18 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby C XX03-C002 | Grid F / 6.4 | Not installed | Not Installed. |  | 5
03 | 03-S19 | Station | PI1004 | Paradigm Inspire 4-button station | Ctrl XX03-1027 | Grid F-G / 9-8 | Installed, untested |  |  | 5
03 | 03-D1 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | OR (Stat) Lab XX03-1108 | Grid East of H / 12-11 | Installed, untested |  |  | 5
03 | 03-D2 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | OR (Stat) Lab XX03-1108 | Grid East of H / 12-11 | Issue | Missing cover. | 13 | 5
03 | 03-D3 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Semi-Restr Corridor XX03-C028 | Grid East of H / 11-10.5 | Installed, untested |  |  | 5
03 | 03-D4 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby B XX03-C003 | Grid B-C / 9.5-9 | Not installed | Not Installed. |  | 5
03 | 03-D5 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | East wing corridor, north | Grid East of H / 9-8 | Installed, untested |  |  | 5
03 | 03-D6 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | East wing corridor, north-east | Grid East of H / 9-8 | Installed, untested |  |  | 5
03 | 03-D7 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | East wing corridor, south | Grid East of H / 9-8 | Installed, untested |  |  | 5
03 | 03-D8 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX03-C014A | Grid East of H / 8 | Not installed | Not Installed - wire at ceiling. | 14 | 5
03 | 03-D9 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby C XX03-C002 | Grid F-G / 5.2 | Not installed | Not Installed. |  | 5
03 | 03-D10 | Sensor | P-LS | Paradigm light sensor | Semi-Restr Corridor XX03-C027 | Grid G-G.9 / 11-10.5 | Not installed | Not Installed. |  | 5
04 | 04-01 | Relay panel | CT04LCPA | Echo ERP-FT-241P (24x20 relays) | Elec XX04-1E04 | Grid F-G / 9.5 | Issue | Missing 1x ERP-RTO card + jumper. 0-10V not landed. Level 06 DMX not run. | 1 | 6
04 | 04-02 | EBDK | EBDK | Emergency Bypass Detection Kit (CT04LCPA) | Elec XX04-1E04 | Grid F-G / 9.5 | Issue | No sense feed. | 1 | 6
04 | 04-03 | Relay panel | CT04LCPB | Echo ERP-FT-241P (24x20 relays) | Elec XX04-1E01 | Grid E / 7.5; Next to Pre-Action XX04-2P01 | Issue | Missing ERP-RTO card + jumper. 1 DMX run from Level 03, not terminated; no term kit. 0-10V not landed. 1 network run from Level 03, origin unknown. | 14 | 6
04 | 04-04 | EBDK | EBDK | Emergency Bypass Detection Kit (CT04LCPB) | Elec XX04-1E01 | Grid E / 7.5 | Installed, untested |  | 14 | 6
04 | 04-05 | NSPS | P-NSPS-D-KIT | Paradigm network station power supply | Elec XX04-1E01 | Grid E / 7 | Not installed | Not Installed. 2 network runs and 2 Unison runs hanging outside conduit in the electrical room; Unison runs are DMX cable and need to be re-pulled. | 14 | 6
04 | 04-06 | Foundry panel | UFMP8 | Foundry 8-circuit panel | Conf XX04-3108A/B | Grid A-B / 6.6 | Issue | Installed, no DMX, loads landed | 16 | 6
04 | 04-07 | Sensor | UHCI-WM | Unison partition sensor | Conf XX04-3108A/B | Grid A-B / 6.8 | Not installed | Not Installed. |  | 6
04 | 04-08 | Sensor | Partition sensors | Partition wall sensors | Conf XX04-3108A/B | Grid A-B / 6.6 | Not installed | Not Installed. |  | 6
04 | 04-S1 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor at Stair A XX04-2S01 | Grid C-D / 13; At stair door | Issue | Wire nuts, wrong wire type. | 2 | 6
04 | 04-S2 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor near Stair D XX04-3S03 | Grid A / 10.5-10; Grid 10-10.5 | Issue | Wire nuts, wrong wire type. | 3 | 6
04 | 04-S3 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Corridor XX04-C026 | Grid F / 11 | Not installed | Not Installed - no box. | 12 | 6
04 | 04-S4 | Station | PI1104 | Paradigm Inspire 4-button station w/ fader | Consult XX04-1104 / IDF XX04-1I03 wall, Corridor XX04-C039 | Grid East of H / 7.5-7; At column | Not installed | Not Installed - no box. | 4 | 6
04 | 04-S5 | Station | PI1002 | Paradigm Inspire 2-button station | Passage XX04-C021 | Grid C / 9.5-9; By Elevator Lobby B | Installed, untested |  |  | 6
04 | 04-S6 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor outside Pharm XX04-1106 / Vest XX04-C029 | Grid East of H / 9 | Not installed | Not Installed - nothing at drawn location; empty boxes on opposite wall, station may have been relocated. Confirm. | 5 | 6
04 | 04-S7 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor north branch at Pre-Action XX04-3P01 | Grid C-D / 8 | Issue | Wire nuts, wrong wire type. |  | 6
04 | 04-S8 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX04-C013 | Grid C / 8-7.5; South wall, west, by Off. Pre-Op Mgr XX04-3102 | Issue | Wire nuts, wrong wire type. |  | 6
04 | 04-S9 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX04-C013 | Grid C-D / 8-7.5; South wall, east | Issue | Wire nuts, wrong wire type. |  | 6
04 | 04-S10 | Station | PI1002 | Paradigm Inspire 2-button station | Passage XX04-C010 | Grid B-C / 5.2; By Elec XX04-3E03 | Issue | Wire nuts, wrong wire type. |  | 6
04 | 04-S11 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX04-C014 at Pre-Action XX04-1P01 | Grid G / 8-7.5 | Not installed | Not Installed - box present. | 6 | 6
04 | 04-S12 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor near Elevator Lobby A XX04-C001 | Grid G / 7.5-7; By Elevator CT-A7 | Not installed | Not Installed - no box; wall under construction (scaffold). | 7 | 6
04 | 04-S13 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX04-C004A | Grid E-F / 6.4; By Passage XX04-C005 | Issue | Wire nuts, wrong wire type, no ground (DMX used as ground). | 8 | 6
04 | 04-S14 | Station | PI1002 | Paradigm Inspire 2-button station | Elevator Lobby C XX04-C002 | Grid F / 6.4 | Not installed | Not Installed - box present. | 9 | 6
04 | 04-S15 | Station | PI1004 | Paradigm Inspire 4-button station | Conf XX04-3108B | Grid A / 6.8 | Issue | Wire nuts, wrong wire type. |  | 6
04 | 04-S16 | Station | PI1004 | Paradigm Inspire 4-button station | Conf XX04-3108A | Grid A-B / 6.8 | Issue | Wire nuts, wrong wire type. |  | 6
04 | 04-D1 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby B XX04-C003 | Grid B-C / 9.5-9 | Not installed | Not Installed. |  | 6
04 | 04-D2 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Conf XX04-3108B | Grid A-B / 6.6 | Not installed | Not Installed. | 15 | 6
04 | 04-D3 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Conf XX04-3108A | Grid A-B / 6.6 | Not installed | Not Installed. | 15 | 6
04 | 04-D4 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Elevator Lobby C XX04-C002 | Grid F / 5.2 | Not installed | Not Installed - ceiling open. | 10 | 6
04 | 04-D5 | Sensor | P-DOC-SM2 | Paradigm wall occupancy sensor | Passage XX04-C021 | Grid C-D / 9.5; By Elevator Lobby B | Issue | Wire nuts, wrong wire type. | 11 | 6
04 | 04-D6 | Sensor | P-DOC-SM2 | Paradigm wall occupancy sensor | Corridor XX04-C023 at Stair D XX04-3S03 | Grid A-B / 10-9.5 | Issue | Wire nuts, wrong wire type, no ground (DMX used as ground). Sticky buttons | 13 | 6
04 | 04-D7 | Sensor | P-LS | Paradigm light sensor | Corridor XX04-C028 | Grid G-G.9 / 10.5 | Not installed | Not Installed - no ceiling. |  | 6
06 | 06-S1 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C007 | North end, at Shaft 1 / Stair XX06-2S01 door | Installed, untested |  | 4 | 7
06 | 06-S2 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C006 | North of match line 1/Ef.106.E, across from Decon XX06-2014 | Not installed | Not Installed - no wire. Box present with blank plate. | 5 | 7
06 | 06-S3 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C006 | North of match line, ~6 ft east of #2, across from ALC PPE XX06-2016 | Not installed | Not Installed — no box. | 6 | 7
06 | 06-S4 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C006 | West end, south of match line | Installed, untested |  |  | 7
06 | 06-S5 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C006 | East end, by C3 fixture near ALC XX06-2012 | Installed, untested |  |  | 7
06 | 06-S6 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C005 | At Shaft 6 / Shaft 7 door | Installed, untested |  |  | 7
06 | 06-S7 | Station | PI1002 | Paradigm Inspire 2-button station | Corridor XX06-C005 | East leg, by elevator | Installed, untested |  |  | 7
06 | 06-D1 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C007 | North end, by Shaft 1 door | Installed, untested |  |  | 7
06 | 06-D2 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C007 | Mid, by Off. MM XX06-2036 | Installed, untested |  |  | 7
06 | 06-D3 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C007 | South, by Lckr/Tlt Stf XX06-2032 | Installed, untested |  |  | 7
06 | 06-D4 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C007 | South end at match line, by Detergent room | Installed, untested |  |  | 7
06 | 06-D5 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C006 | West | Installed, untested |  |  | 7
06 | 06-D6 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C006 | Mid, by ALC XX06-2012 | Installed, untested |  |  | 7
06 | 06-D7 | Sensor | P-DOC-C-LR | Paradigm ceiling occupancy sensor | Corridor XX06-C006 | East, by C20 fixture | Installed, untested |  |  | 7
06M | 06M-01 | Equipment rack | Equipment Rack 18U | Unison ERn4-RM rack | Stair A Vestibule XX06M-2SV01 area | C/13 | Issue | Missing 1x 1U brush panel and 1x ERn blank | 1, 2 | 8
06M | 06M-02 | Relay panel | CT06LCPB | Echo ERP-FT-241P (24x20 relays) | Stair A Vestibule XX06M-2SV01 area, right of rack | C/13 | Issue | Missing 1x ERP-FT-LVD (0-10V card); 0-10V not landed. Both DMX cables not run. | 1 | 8
06M | 06M-03 | EBDK | EBDK | Emergency Bypass Detection Kit | Below CT06LCPB | C/13 | Installed, untested |  | 3 | 8
06M | 06M-04 | Foundry panel | CT06LCPA | Foundry UFMP8 | Near Elevator Machine Room XX06M-1EM02 | D–E/11 | Issue | Only one of two DMX runs pulled (which one undetermined) |  | 8

## Connections
Connections
Levels B2-06
Level | ID | From | Cable | To | Qty | Status | Note | Floor Order
B2 | C-01 | CTB2LCPB | X | DMX to Level B1 CTB1LCPB | 1 | Issue | Run, not terminated; no term kit. Survey drawing showed Level 01 | 1
B2 | C-02 | CTB2LCPB | 0-10V | Fixtures | 1 | Not installed | Not run | 1
B2 | C-03 | CTB2LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 1
B2 | C-04 | 120v Power | 120V | P-NSPS-D Power Supply | 1 | Not installed | Not run | 1
B2 | C-05 | P-NSPS-D | N | Network to Level 01 | 1 | Issue | Lands in ERP; needs to be run down to the NSPS below it | 1
B2 | C-06 | P-NSPS-D | U | Unison to Level B1 Devices | 1 | Issue | Lands in ERP? (Not labeled); needs to be run down to the NSPS below it | 1
B2 | C-07 | Station & sensor | U | B2 Devices to P-NSPS-D |  | Issue | Lands in ERP; needs to be run down to the NSPS below it | 1
B2 | C-08 | P-NSPS-D | U | Unison from B2 station & sensor |  | Issue | Lands in ERP; needs to be run down to the NSPS below it | 1
B1 | C-01 | CTB1LCPB | X | DMX to Level 01 | 1 | Issue | Run, not terminated; no term kit | 2
B1 | C-02 | CTB1LCPB | X | DMX to Level B2 | 1 | Issue | Run, not terminated; no term kit | 2
B1 | C-03 | CTB1LCPB | 0-10V | Fixtures | 1 | Not installed | Not run | 2
B1 | C-04 | CTB1LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 2
B1 | C-05 | Stations & sensors | U | Unison to Level B2 ERP |  | Issue | Lands in B2 ERP; needs to be run down to the NSPS below it | 2
01 | C-01 | CT01LCPB | X | DMX to Level 02 UFMP4 | 1 | Installed, untested | Terminated, untested | 3
01 | C-02 | CT01LCPB | X | DMX to Equipment rack | 1 | Installed, untested | Terminated, untested | 3
01 | C-03 | CT01LCPB | 0-10V | Fixtures | 1 | Issue | Run, not terminated | 3
01 | C-04 | CT01LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 3
01 | C-05 | CT01LCPA | X | DMX to Level 02 | 1 | Installed, untested | Terminated, untested | 3
01 | C-06 | CT01LCPA | X | DMX to Equipment rack | 1 | Installed, untested | Terminated, untested | 3
01 | C-07 | CT01LCPA | 0-10V | Fixtures | 1 | Issue | Run, not terminated | 3
01 | C-08 | CT01LCPA | P | EBDK panic wire | 1 | Installed, untested |  | 3
01 | C-09 | Equipment rack | X | DMX to B3A Canyon | 1 | Not installed | One DMX wire at equipment rack unidentified. Could be this?; no term kit | 3
01 | C-10 | Equipment rack | X | DMX to C13A Oculus | 1 | Not installed | One DMX wire at equipment rack unidentified. Could be this?; no term kit | 3
01 | C-11 | Equipment rack | X | DMX to D1 ED Column Capital | 1 | Not installed | One DMX wire at equipment rack unidentified. Could be this?; no term kit | 3
01 | C-12 | Equipment rack | X | DMX to UFMP4 (7) | 1 | Not installed | One DMX wire at equipment rack unidentified. Could be this?; no term kit | 3
01 | C-13 | Equipment rack | N | Walter Tower ETC P-CCS | 1 | Not installed | Not installed, Walter tower conduit empty | 3
01 | C-14 | Equipment rack | N | Level 02 | 1 | Issue | Net run, not terminated; destination might be wrong room | 3
01 | C-15 | Equipment rack | F | Equipment rack Level 06 | 1 | Issue | Fiber terminated; missing kit parts SGM1612, SGN1021 | 3
01 | C-16 | Equipment rack | NG | P-TS7-E touchscreen | 1 | Not installed | P-TS7-E not installed | 3
01 | C-17 | Stations & sensor | U | Devices to equipment rack |  | Not installed | No unison wire at equipment rack | 3
01 | C-18 | Equipment rack | X | DMX to CT01LCPB | 1 | Issue | Run, not terminated at rack; no term kit | 3
01 | C-19 | Equipment rack | X | DMX to CT01LCPA | 1 | Issue | Run, not terminated at rack; no term kit | 3
01 | C-20 | Equipment rack | X | DMX to Level B1 CTB1LCPB | 1 | Issue | Run, not terminated; no term kit (per Level B1). Likely the unidentified DMX wire at the rack? | 3
01 | C-21 | Equipment rack | N | Network to Level B2 P-NSPS-D | 1 | Issue | Run (per Level B2) | 3
01 | C-22 | Equipment rack | U | Unison from stations & sensors |  | Not installed | No Unison wire at equipment rack | 3
01 | C-23 | UFMP4 (7) | X | DMX to equipment rack | 1 | Not installed | UFMP4s not installed; one DMX wire at the rack unidentified, could be this? | 3
01 | C-24 | P-TS7-E | NG | Network & ground to equipment rack | 1 | Not installed | P-TS7-E not installed | 3
01 | C-25 | 120v Power | 120V | Equipment rack | 1 | Issue | Box not closed; wire landed | 3
02 | C-01 | CT02LCPA | X | DMX to Level 03 | 1 | Issue | One of the two LCPA DMX wires missing, which one undetermined; no term kit | 4
02 | C-02 | CT02LCPA | X | DMX to Level 01 | 1 | Issue | One of the two LCPA DMX wires missing, which one undetermined; no term kit | 4
02 | C-03 | CT02LCPA | 0-10V | Fixtures | 1 | Issue | Run, not terminated | 4
02 | C-04 | CT02LCPA | P | EBDK panic wire | 1 | Installed, untested |  | 4
02 | C-05 | CT02LCPB | X | DMX to Level 03 | 1 | Issue | Run, not terminated; no term kit | 4
02 | C-06 | CT02LCPB | X | DMX to UFMP4 | 1 | Issue | Run, not terminated; no term kit; UFMP4 not installed | 4
02 | C-07 | CT02LCPB | 0-10V | Fixtures | 1 | Not installed | Not run | 4
02 | C-08 | CT02LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 4
02 | C-09 | Stations & sensors | U | Devices to P-NSPS-D |  | Not installed | Not run; P-NSPS-D not installed; have not found unison wire location | 4
02 | C-10 | P-NSPS-D | N | Network to Level 01 equipment rack | 1 | Issue | Run found at CT02LCPB in Elec XX02-1E02; riser lands it at the P-NSPS-D in Elec XX02-1E01 | 4
02 | C-11 | UFMP4 | X | DMX to Level 01 CT01LCPB | 1 | Issue | Run (terminated at CT01LCPB on Level 01); UFMP4 not installed | 4
02 | C-12 | UFMP4 | X | DMX to CT02LCPB | 1 | Issue | Run, not terminated; no term kit; UFMP4 not installed (per C-06) | 4
02 | C-13 | P-NSPS-D | U | Unison from stations & sensors |  | Not installed | Not run; P-NSPS-D not installed; have not found unison wire location | 4
02 | C-14 | 120v Power | 120V | P-NSPS-D Power Supply | 1 | Not installed | Not run | 4
03 | C-01 | CT03LCPA | X | DMX to UFMP4s | 1 | Issue | Run, not terminated; no term kit. Survey drawing showed Level 04 | 5
03 | C-02 | CT03LCPA | X | DMX to Level 02 | 1 | Issue | Run, not terminated; no term kit | 5
03 | C-03 | CT03LCPA | 0-10V | Fixtures | 1 | Issue | Not landed | 5
03 | C-04 | CT03LCPA | P | EBDK panic wire | 1 | Installed, untested |  | 5
03 | C-05 | CT03LCPA | N | Network | 2 | Issue | Run; destination unknown. One may be the P-NSPS-D network to Level 06? | 5
03 | C-06 | CT03LCPB | X | DMX to Level 04 | 1 | Issue | Run, not terminated; no term kit | 5
03 | C-07 | CT03LCPB | X | DMX to Level 02 | 1 | Issue | Run, not terminated; no term kit | 5
03 | C-08 | CT03LCPB | 0-10V | Fixtures | 1 | Issue | Not landed | 5
03 | C-09 | CT03LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 5
03 | C-10 | UFMP4 #1, #2 | X | DMX to Level 04 CT04LCPA | 1 | Issue | Run, not terminated; no term kit. Survey drawing showed Level 06 (2 runs) | 5
03 | C-11 | 120v Power | 120V | P-NSPS-D Power Supply | 1 | Issue | Needs landing | 5
03 | C-12 | Stations & sensors | U | Devices to P-NSPS-D |  | Installed, untested | # of runs not verified | 5
03 | C-13 | UFMP4 #1, #2 | X | Missing DMX run (one per UFMP4) | 2 | Not installed | Not run; which is missing? Level 04 CT04LCPB DMX may come from a Level 03 UFMP4? Riser: missing run may be the link between UFMP4 #1 and #2? | 5
03 | C-14 | UFMP4 #1, #2 | X | DMX to CT03LCPA | 1 | Issue | Run, not terminated; no term kit (per C-01) | 5
03 | C-15 | P-NSPS-D | N | Network to Level 06 equipment rack | 1 | Issue | Not found at the P-NSPS-D; may be one of the 2 network runs at CT03LCPA (NSPS moved from Elec XX03-1E01)? | 5
03 | C-16 | P-NSPS-D | U | Unison from stations & sensors |  | Installed, untested | # of runs not verified | 5
04 | C-01 | CT04LCPA | X | DMX to Level 06 | 1 | Not installed | Not run; no term kit | 6
04 | C-02 | CT04LCPA | X | DMX to Level 03 UFMP4s | 1 | Issue | Run, not terminated; no term kit | 6
04 | C-03 | CT04LCPA | 0-10V | Fixtures | 1 | Issue | Not landed | 6
04 | C-04 | CT04LCPA | P | EBDK panic wire | 1 | Installed, untested |  | 6
04 | C-05 | CT04LCPB | X | DMX to Level 03 CT03LCPB | 1 | Issue | Run, not terminated; no term kit. May come from the Level 03 UFMP4? | 6
04 | C-06 | CT04LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 6
04 | C-07 | UFMP8 | X | DMX from Level 06 | 1 | Not installed | Not run, term kit in box | 6
04 | C-08 | UHCI-WM | UV | To Level 06 | 1 | Not installed | Potential Aux 24v hanging outside of conduit in 1E01 next to CT04LCPB. Need to confirm origin | 6
04 | C-09 | Stations & sensors | U | Devices to P-NSPS-D |  | Issue | 2 runs outside conduit; need to be rerun with proper wire (not dmx) | 6
04 | C-10 | P-NSPS-D | N | Network to Level 06 | 1 | Issue | Run, not terminated; hanging outside conduit | 6
04 | C-11 | CT04LCPB | 0-10V | Fixtures | 1 | Issue | Not landed | 6
04 | C-12 | CT04LCPB | N | Network from Level 03 | 1 | Issue | Run; origin unknown. Not on riser; may be the Level 03 P-NSPS-D network to Level 06 passing through? | 6
04 | C-13 | P-NSPS-D | U | Unison from stations & sensors |  | Issue | 2 runs outside conduit; need to be rerun with proper wire (not dmx) | 6
04 | C-14 | 120v Power | 120V | P-NSPS-D Power Supply | 1 | Not installed | Not run | 6
06 | C-10 | PI1002 & P-DOC-C-LR stations | U | Unison to equipment rack |  | Issue | 4 run, not terminated | 7
06M | C-01 | Equipment rack | X | DMX to B3B Elev Core C fixture | 1 | Not installed | Not run; no term kit | 8
06M | C-02 | Equipment rack | X | DMX to B7 Stair A fixture | 1 | Not installed | Not run; no term kit | 8
06M | C-03 | Equipment rack | X | Spare DMX out | 2 | Not installed | Not run; no term kit | 8
06M | C-04 | Equipment rack | N | ERn4 Level 16 | 2 | Issue | Run, not terminated | 8
06M | C-05 | Equipment rack | F | Equipment rack Level 28 | 1 | Not installed | Not run | 8
06M | C-06 | Equipment rack | F | Equipment rack Level 01 | 1 | Issue | Run, not terminated; missing kit parts: SGN1253, SGM1612, SGN1021 | 8
06M | C-07 | CT06LCPB | X | DMX to Level 09 | 1 | Not installed | Not run; no term kit | 8
06M | C-08 | CT06LCPB | P | EBDK panic wire | 1 | Installed, untested |  | 8
06M | C-09 | CT06LCPA | X | DMX to Level 09 | 1 | Issue | Only one of the two CT06LCPA runs pulled, which one undetermined; no term kit | 8
06M | C-11 | CT06LCPB | 0-10V | Fixtures | 1 | Issue | Not landed | 8
06M | C-12 | CT06LCPB | X | DMX to equipment rack | 1 | Not installed | Not run; no term kit | 8
06M | C-13 | CT06LCPA | X | DMX to Level 04 CT04LCPA | 1 | Issue | Only one of the two CT06LCPA runs pulled, which one undetermined (lower level?); Level 04 end shows not run; no term kit | 8
06M | C-14 | Equipment rack | X | DMX to CT06LCPB | 1 | Not installed | Not run; no term kit | 8
06M | C-15 | Equipment rack | U | Unison from Level 06 stations |  | Issue | 4 run, not terminated (per C-10) | 8
06M | C-16 | Equipment rack | N | Network to Level 03 P-NSPS-D | 1 | No access | Not surveyed | 8
06M | C-17 | Equipment rack | N | Network to Level 04 P-NSPS-D | 1 | Issue | Run (per Level 04) | 8
06M | C-18 | Equipment rack | X | DMX to Level 04 UFMP8 | 1 | Not installed | Not run (per Level 04; term kit in box at UFMP8) | 8
06M | C-19 | Equipment rack | UV | UHCI-WM partition sensor, Level 04 | 1 | Not installed | Not run (per Level 04); possible Aux 24V wire in Level 04 Elec XX04-1E01 may be this run? | 8
06M | C-20 | Equipment rack | N | Network to Level 09 | 2 | Not started | Not surveyed | 8
06M | C-21 | Equipment rack | N | Network to Level 10 | 2 | Not started | Not surveyed | 8
06M | C-22 | Equipment rack | N | Network to Level 11 | 2 | Not started | Not surveyed | 8
06M | C-23 | Equipment rack | X | DMX to Level 11 | 1 | Not started | Not surveyed | 8
06M | C-24 | Equipment rack | N | Network to Level 12 | 1 | Not started | Not surveyed | 8
06M | C-25 | 120v Power | 120V | Equipment rack | 1 | Not installed | Not run | 8

## Punch List
Outstanding items
Levels B2-06
Level | # | Device | Item | Type | Photo | Owner | Tracking status | Date closed | Notes | Floor Order
B2 | 1 | CTB2LCPB | Run and land 0-10V control wiring | Cable not run |  | EC | Open |  |  | 1
B2 | 2 | CTB2LCPB | Terminate DMX to Level B1 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 1
B2 | 3 | P-NSPS-D | Land 48V jumper from power supply to NSPS | Wiring | 2 | EC | Open |  | Provided in NSPS box | 1
B2 | 4 | P-NSPS-D | Run 120V to NSPS power supply | Cable not run |  | EC | Open |  |  | 1
B2 | 5 | P-NSPS-D | Run network to P-NSPS-D | Cable not run | 1 | EC | Open |  | Lands in ERP; needs to be run down to the NSPS below it | 1
B2 | 6 | P-NSPS-D | Run Unison to P-NSPS-D (B2 & B1 stations and devices) | Cable not run | 1 | EC | Open |  | 4x Unison land in ERP; need to be run down to the NSPS below it | 1
B2 | 7 | PI1002 S1 - Elevator Lobby B XXB2-C003 east | Install cover | Missing part | 3 | EC | Open |  | Confirm whether on site | 1
B2 | 8 | P-DOC-C-LR D1 - Elevator Lobby B XXB2-C003 | Not installed: install sensor (box present) | Not installed | 4 | EC | Open |  |  | 1
B2 | 9 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 1
B1 | 1 | CTB1LCPB | Install ERP-RTO jumper | Missing part |  | EC | Open |  |  | 2
B1 | 2 | CTB1LCPB | Land panel loads | Termination |  | EC | Open |  |  | 2
B1 | 3 | CTB1LCPB | Run and land 0-10V control wiring | Cable not run |  | EC | Open |  |  | 2
B1 | 4 | CTB1LCPB | Terminate DMX to Level 01 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 2
B1 | 5 | CTB1LCPB | Terminate DMX to Level B2 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 2
B1 | 6 | EBDK (CTB1LCPB) | Provide sense feed to EBDK | Cable not run |  | EC | Open |  |  | 2
B1 | 7 | Stations & sensors | Unison runs land in the Level B2 ERP (CTB2LCPB) | Information |  | EC | Open |  | Need to be run down to the NSPS below it. Unison wire on B2 is unlabeled | 2
B1 | 8 | PI1002 S3 - Corridor XXB1-C005 north | Install cover | Missing part | 10 | EC | Open |  | Confirm whether on site | 2
B1 | 9 | PI1002 S4 - Corridor XXB1-C005 south | Install cover | Missing part | 11 | EC | Open |  | Confirm whether on site | 2
B1 | 10 | PI1002 S5 - Elevator Lobby C XXB1-C002 | Install cover | Missing part |  | EC | Open |  | Confirm whether on site | 2
B1 | 11 | PI1002 S6 - Corridor XXB1-C004 at IDF XXB1-1I05 | Install cover | Missing part |  | EC | Open |  | Confirm whether on site | 2
B1 | 12 | PI1002 S7 - Corridor XXB1-C008 west | Install cover | Missing part |  | EC | Open |  | Confirm whether on site | 2
B1 | 13 | PI1002 S8 - Corridor XXB1-C008 east at Gas Cyldr XXB1-1002 | Install cover | Missing part |  | EC | Open |  | Confirm whether on site | 2
B1 | 14 | PI1002 S9 - Corridor at Drinking Fountain XXB1-1004 | Install cover | Missing part |  | EC | Open |  | Confirm whether on site | 2
B1 | 15 | PI1002 S1 - Elevator Lobby B XXB1-C003 east | Not installed: install station | Not installed |  | EC | Open |  | No box | 2
B1 | 16 | PI1002 S2 - Corridor XXB1-C007 at Stair F XXB1-3S02 | Not installed: install station (box present) | Not installed | 4 | EC | Open |  |  | 2
B1 | 17 | P-DOC-W D1 - Corridor XXB1-C009 at Water Meter XXB1-3WM01 | Not installed: install sensor (box present) | Not installed | 2 | EC | Open |  |  | 2
B1 | 18 | P-DOC-W D2 - Corridor XXB1-C009 at Fan Room XXB1-2F01 | Not installed: install sensor (box present) | Not installed | 3 | EC | Open |  |  | 2
B1 | 19 | P-DOC-W D3 - Elevator Lobby B XXB1-C003 west | Not installed: install sensor | Not installed |  | EC | Open |  | No box | 2
B1 | 20 | P-DOC-C-LR D4 - Elevator Lobby B XXB1-C003 | Not installed: install sensor | Not installed |  | EC | Open |  | No box | 2
B1 | 21 | P-DOC-W D5 - Corridor XXB1-C007 north | Not installed: install sensor (box present) | Not installed | 5 | EC | Open |  |  | 2
B1 | 22 | P-DOC-W D6 - Corridor XXB1-C007 south at Confident Waste XXB1-3017 | Not installed: install sensor (box present) | Not installed | 6 | EC | Open |  |  | 2
B1 | 23 | P-DOC-W D7 - Corridor XXB1-C006 at Cart Wash XXB1-3007 | Not installed: install sensor (box present) | Not installed | 7 | EC | Open |  |  | 2
B1 | 24 | P-DOC-W D8 - Corridor XXB1-C006 at Trash Compactor XXB1-2TC01 | Not installed: install sensor (box present) | Not installed | 8 | EC | Open |  |  | 2
B1 | 25 | P-DOC-C-LR D13 - Corridor XXB1-C008 west | Not installed: install sensor | Not installed | 12 | EC | Open |  |  | 2
B1 | 26 | P-DOC-C-LR D14 - Corridor XXB1-C008 east at Gas Cyldr XXB1-1002 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 2
B1 | 27 | Walter Tower east wing | Gain access; survey 5x PI1002 (S10-S14) and 7x P-DOC-C-LR (D15-D21) in Corridors WTB1-C010, C011, C012, C016 and Fire Protection Closet WTB1-2008 | Access |  | ETC | Open |  | Blocked by Walter Tower barricade | 2
B1 | 28 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 2
01 | 1 | CT01LCPB | Install ERP-RTO jumper | Missing part |  | EC | Open |  |  | 3
01 | 2 | CT01LCPB | Confirm ERP-FT-LVD (0-10V card) is installed | Missed Survey | 14 | ETC | Closed | 2026-10-08 | Needs 2x 0-10v cards, only one installed | 3
01 | 3 | CT01LCPB | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 3
01 | 4 | CT01LCPA | Confirm ERP-FT-LVD (0-10V card) is installed | Missed Survey |  | ETC | Closed | 2026-10-08 | Needs 2x 0-10v cards, only one installed | 3
01 | 5 | CT01LCPA | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 3
01 | 6 | EBDK (CT01LCPA) | Check sense feed to EBDK | Missed Survey |  | ETC | Closed | 2026-10-08 | Terminated | 3
01 | 7 | Equipment rack | Install 1U brush panel | Missing part |  | EC/ETC | Open |  |  | 3
01 | 8 | Equipment rack | Terminate fiber to Equipment rack Level 06 | Termination |  | EC/ETC | In progress |  | Fiber terminated in equipment rack; missing kit parts SGM1612, SGN1021 | 3
01 | 9 | Equipment rack | Survey outgoing runs (DMX x4, network x2, fiber, NG) and check Unison wiring at each device | Missed Survey |  | ETC | Closed | 2026-10-08 | Connections list updated | 3
01 | 10 | P-TS7-E - Info Desk WT01-1046 | Not installed: install touchscreen | Not installed |  | EC | Open |  |  | 3
01 | 11 | UFMP4 - Vest WT01-1044 | Not installed: install UFMP4 | Not installed |  | EC | Open |  |  | 3
01 | 12 | UFMP4 - BH OBS RM 47 | Not installed: install UFMP4 | Not installed |  | EC | Open |  |  | 3
01 | 13 | UFMP4 - BH OBS RM 48 | Not installed: install UFMP4 | Not installed |  | EC | Open |  |  | 3
01 | 14 | UFMP4 - BH OBS RM 49 | Not installed: install UFMP4 | Not installed | 5 | EC | Open |  | Unit mounted above ceiling, but not installed otherwise | 3
01 | 15 | UFMP4 - BH OBS RM 50 | Not installed: install UFMP4 | Not installed |  | EC | Open |  | Unit mounted above ceiling, but not installed otherwise | 3
01 | 16 | UFMP4 - BH OBS RM 51 | Not installed: install UFMP4 | Not installed |  | EC | Open |  | Unit mounted above ceiling, but not installed otherwise | 3
01 | 17 | UFMP4 - BH OBS RM 52 | Not installed: install UFMP4 | Not installed |  | EC | Open |  | Unit mounted above ceiling, but not installed otherwise | 3
01 | 18 | PI1002 S2 - Corridor XX01-C018 | Replace wire nuts with Wagos (provided in box) | Wiring |  | EC | Open |  |  | 3
01 | 19 | PI1104 S4 - Discharge XX01-2106 | Replace wire nuts with Wagos (provided in box) | Wiring |  | EC | Open |  |  | 3
01 | 20 | PI1104 S15 - Hydra XX01-3137 | Replace wire nuts with Wagos (provided in box) | Wiring | 1 | EC | Open |  |  | 3
01 | 21 | PI1002 S19 - Corridor XX01-C004 | Replace wire nuts with Wagos (provided in box) | Wiring | 2 | EC | Open |  |  | 3
01 | 22 | PI1104 S5 - Info Desk WT01-1046 | Not installed: install station | Not installed | 9 | EC | Open |  |  | 3
01 | 23 | PI1104 S7 - BH OBS RM 47 | Not installed: install station | Not installed |  | EC | Open |  |  | 3
01 | 24 | PI1104 S8 - Passageway at BH OBS RM 48 | Not installed: install station | Not installed | 6 | EC | Open |  |  | 3
01 | 25 | PI1104 S9 - Passageway at BH OBS RM 49 | Not installed: install station | Not installed | 6 | EC | Open |  |  | 3
01 | 26 | PI1104 S10 - Passageway at BH OBS RM 50 | Not installed: install station | Not installed | 6 | EC | Open |  |  | 3
01 | 27 | PI1104 S11 - Passageway at BH OBS RM 51 | Not installed: install station | Not installed | 6 | EC | Open |  |  | 3
01 | 28 | PI1104 S12 - Passageway at BH OBS RM 52 | Not installed: install station | Not installed | 6 | EC | Open |  |  | 3
01 | 29 | PI1104 S8-S12 - BH OBS passageway | 3-gang box installed for 1-gang switch at each BH OBS station | Information | 6 | EC | Open |  |  | 3
01 | 30 | PI1104 S13 - ALC. HW WT01-C024A | Not installed: install station (box present) | Not installed | 4 | EC | Open |  |  | 3
01 | 31 | PI1104 S14 - Passageway WT01-C023 | Not installed: install station (box present) | Not installed | 7 | EC | Open |  |  | 3
01 | 32 | PI1004 S16 - Corridor XX01-C015 | Not installed: install station (box present) | Not installed | 3 | EC | Open |  |  | 3
01 | 33 | PI1104 S22 - Tlt. Pat Stf WT01-2161 | Not installed: install station (box present) | Not installed | 8 | EC | Open |  |  | 3
01 | 34 | P-DOC-C-LR D1 - Elevator Lobby C XX01-C002 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 3
01 | 35 | PI1002 S6 - Humidifier Closet WT01-2033 | Check device | Missed Survey |  | ETC | Open |  | Blocked | 3
01 | 36 | PI1002 S21 - Passage XX01-C005A | Check device | Missed Survey |  | ETC | Closed | 2026-10-08 | Device list updated | 3
01 | 37 | PI1004 S18, PI1104 S20 | Check devices | Missed Survey |  | ETC | Closed | 2026-10-08 | Device list updated | 3
01 | 38 | CT01LCPB | Install ERP-FT-LVD (0-10V card) | Missing part | 14 | EC | Open |  | Needs 2x 0-10V cards, only one installed | 3
01 | 39 | CT01LCPA | Install ERP-FT-LVD (0-10V card) | Missing part | 15 | EC | Open |  | Needs 2x 0-10V cards, only one installed | 3
01 | 40 | Equipment rack | Terminate DMX from CT01LCPB | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 3
01 | 41 | Equipment rack | Terminate DMX from CT01LCPA | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 3
01 | 42 | Equipment rack | Run DMX to B3A Canyon | Cable not run |  | EC | Open |  |  | 3
01 | 43 | Equipment rack | Run DMX to C13A Oculus | Cable not run |  | EC | Open |  |  | 3
01 | 44 | Equipment rack | Run DMX to D1 ED Column Capital | Cable not run |  | EC | Open |  |  | 3
01 | 45 | Equipment rack | Run DMX to UFMP4s | Cable not run |  | EC | Open |  |  | 3
01 | 46 | Equipment rack | Identify unidentified DMX wire at rack | Information | 12 | EC | Open |  | One of the four outgoing DMX runs? Riser: likely the Level B1 run | 3
01 | 47 | Equipment rack | Run network to Walter Tower ETC P-CCS | Cable not run |  | EC | Open |  | Walter Tower conduit empty | 3
01 | 48 | Equipment rack | Terminate network to Level 02 | Termination |  | ETC | Open |  | Destination might be wrong room? | 3
01 | 49 | Stations & sensors | Run Unison to equipment rack | Cable not run |  | EC | Open |  | No Unison wire at equipment rack | 3
01 | 50 | Equipment rack | Secure 120V box | Wiring | 12 | EC | Open |  | 120V run and terminated; box not secured | 3
01 | 51 | PI1004 S18 - SLD HLD WT01-2001 | Not installed: install station (box present) | Not installed | 11 | EC | Open |  | Wire present, no ground; provide ground | 3
01 | 52 | PI1104 S20 - NS WT01-2101 | Not installed: install station (box present) | Not installed | 10 | EC | Open |  | Wire present, no ground; provide ground | 3
01 | 53 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 3
02 | 1 | CT02LCPA | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 4
02 | 2 | CT02LCPA | Check (2) 0-10V headers | Missed Survey | 6 | ETC | Closed | 2026-10-08 | Headers installed | 4
02 | 3 | CT02LCPA | Pull missing DMX wire | Cable not run |  | EC | Open |  | Level 03 or Level 01 run, which one undetermined | 4
02 | 4 | CT02LCPA | Terminate DMX to Level 03 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 4
02 | 5 | CT02LCPA | Terminate DMX to Level 01 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 4
02 | 6 | EBDK (CT02LCPA) | Provide sense feed to EBDK | Cable not run |  | EC | Open |  |  | 4
02 | 7 | P-NSPS-D - Elec XX02-1E01 | Not installed: install P-NSPS-D and land 120V and Unison wire | Not installed |  | EC | Open |  | Unison wire location not found | 4
02 | 8 | CT02LCPB | Run and land 0-10V control wiring | Cable not run | 1 | EC | Open |  |  | 4
02 | 9 | CT02LCPB | Terminate DMX to Level 03 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 4
02 | 10 | CT02LCPB | Terminate DMX to UFMP4 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 4
02 | 11 | EBDK (CT02LCPB) | Provide sense feed to EBDK | Cable not run |  | EC | Closed | 2026-10-08 | Sense run and terminated | 4
02 | 12 | UFMP4 - Elec XX02-1E02 | Not installed: install UFMP4 | Not installed |  | EC | Open |  |  | 4
02 | 13 | PI1002 S2 - Reception XX02-2009 | Check station, stuck buttons | Missed Survey |  | ETC | Open |  |  | 4
02 | 14 | PI1002 S9 - Corridor at Tlt. Stf XX02-1020 | Spot check: Wagos used like wire nuts, wire stripped too long; re-terminated on site | Information | 2 | ETC | Closed |  | Reterminated - all good | 4
02 | 15 | PI1002 S1 - Corridor at Pre-Action XX02-2P01 | Not installed: install station | Not installed |  | EC | Open |  |  | 4
02 | 16 | PI1002 S5 - Central Supply WT02-2033 west | Not installed: install station | Not installed |  | EC | Open |  |  | 4
02 | 17 | PI1104 S12 - Seating XX02-C016 | Not installed: install station | Not installed |  | EC | Open |  |  | 4
02 | 18 | PI1002 S13 - Corridor XX02-C004 | Not installed: install station | Not installed |  | EC | Open |  |  | 4
02 | 19 | PI1002 S14 - Elevator Lobby C XX02-C002 | Not installed: install station | Not installed |  | EC | Open |  |  | 4
02 | 20 | P-DOC-C-LR D1 - Corridor XX02-C011 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 4
02 | 21 | P-DOC-C-LR D4 - Corridor XX02-C010 | Not installed: install sensor | Not installed | 3 | EC | Open |  |  | 4
02 | 22 | P-DOC-C-LR D4 - Corridor XX02-C010 | Confirm existing sensor at location is a Wattstopper, not a P-DOC | Information | 3 | EC | Open |  | Shows P-DOC on DWG, Wattstopper installed. Confirm? | 4
02 | 23 | P-DOC-C-LR D10 - Corridor XX02-C008 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 4
02 | 24 | P-DOC-C-LR D11 - Central Supply WT02-2033 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 4
02 | 25 | P-DOC-C-LR D23 - Corridor XX02-C004 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 4
02 | 26 | P-DOC-C-LR D24 - Elevator Lobby C XX02-C002 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 4
02 | 27 | PI1002 S11 - Elevator Lobby A XX02-C001 | Check device | Missed Survey |  | ETC | Closed | 2026-10-08 | Updated device list. | 4
02 | 28 | PI1002 S15 - East corridor south of Seating | Check device | Missed Survey |  | ETC | Closed | 2026-10-08 | Updated device list. | 4
02 | 29 | CT02LCPB | Identify purpose of network run from Level 01 | Information |  | EC | Open |  | 1 net run from Level 01; for what? Riser: network for the P-NSPS-D in Elec XX02-1E01 | 4
02 | 30 | PI1002 S11 - Elevator Lobby A XX02-C001 | Not installed: install box, pull wire, install station | Not installed | 4 | EC | Open |  |  | 4
02 | 31 | PI1002 S15 - East corridor south of Seating | Not installed: install box, pull wire, install station | Not installed |  | EC | Open |  |  | 4
02 | 32 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 4
03 | 1 | CT03LCPA | Install new I/O card | Replace Part |  | EC | Open |  | Part number to follow | 5
03 | 2 | CT03LCPA | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 5
03 | 3 | CT03LCPA | Terminate DMX to UFMP4s | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 5
03 | 4 | CT03LCPA | Terminate DMX to Level 02 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 5
03 | 5 | CT03LCPA | Identify purpose of 2 network runs | Information |  | EC | Open |  | 2 nets run, where do they go? One may be the P-NSPS-D network to Level 06? | 5
03 | 6 | CT03LCPB | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 5
03 | 7 | CT03LCPB | Terminate DMX to Level 04 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 5
03 | 8 | CT03LCPB | Terminate DMX to Level 02 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 5
03 | 9 | P-NSPS-D | Land 120V power | Termination |  | EC | Open |  |  | 5
03 | 10 | UFMP4 #1 - Semi-Restr Corridor XX03-C028 | Terminate DMX | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 5
03 | 11 | UFMP4 #2 - Semi-Restr Corridor XX03-C028 | Terminate DMX | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 5
03 | 12 | UFMP4 #1, #2 | Check whether DMX has a through | Missed Survey |  | ETC | Closed | 2026-10-08 | Verified only one DMX run to each UFMP4 | 5
03 | 13 | PI1104 S4 - Semi-Restr Corridor XX03-C028 | Install cover | Missing part | 5 | EC | Open |  | Confirm whether on site | 5
03 | 14 | PI1104 S6 - ALC. Stretcher XX03-2094 | Replace station (trim cut, broken) | Replace Part | 7, 8 | EC | Open |  |  | 5
03 | 15 | PI1104 S9 - Reception / Info Desk XX03-2102 | Install cover | Missing part | 10 | EC | Open |  | Confirm whether on site | 5
03 | 16 | P-DOC-C-LR D2 - OR (Stat) Lab XX03-1108 | Install cover | Missing part | 13 | EC | Open |  | Confirm whether on site | 5
03 | 17 | PI1104 S8 - Corridor XX03-C014A | Not installed: install station (box present) | Not installed | 9 | EC | Open |  |  | 5
03 | 18 | PI1002 S11 - Semi-Restr Corridor XX03-C028 north | Not installed: install station | Not installed |  | EC | Open |  |  | 5
03 | 19 | PI1002 S12 - Semi-Restr Corridor XX03-C028 at Frozen Section | Not installed: install station | Not installed |  | EC | Open |  |  | 5
03 | 20 | PI1002 S13 - Elevator Lobby B XX03-C003 | Not installed: install station (box present) | Not installed | 12 | EC | Open |  |  | 5
03 | 21 | PI1002 S18 - Elevator Lobby C XX03-C002 | Not installed: install station | Not installed |  | EC | Open |  |  | 5
03 | 22 | P-DOC-C-LR D4 - Elevator Lobby B XX03-C003 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 5
03 | 23 | P-DOC-C-LR D8 - Corridor XX03-C014A | Not installed: install sensor (wire at ceiling) | Not installed | 14 | EC | Open |  |  | 5
03 | 24 | P-DOC-C-LR D9 - Elevator Lobby C XX03-C002 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 5
03 | 25 | P-LS D10 - Semi-Restr Corridor XX03-C027 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 5
03 | 26 | PI1002 S15, S16 - Corridor XX03-C014 | Check devices | Missed Survey |  | ETC | Closed | 2026-10-08 | Updated device list | 5
03 | 27 | UFMP4 #1 - Semi-Restr Corridor XX03-C028 | Pull missing DMX cable | Cable not run | 15 | EC | Open |  | Only one DMX run to each UFMP4; which is missing? | 5
03 | 28 | UFMP4 #2 - Semi-Restr Corridor XX03-C028 | Pull missing DMX cable | Cable not run | 15 | EC | Open |  | Only one DMX run to each UFMP4; which is missing? | 5
03 | 29 | PI1002 S15 - Corridor XX03-C014 north | Not installed: install station (box present) | Not installed | 16 | EC | Open |  |  | 5
03 | 30 | PI1002 S16 - Corridor XX03-C014 south | Not installed: install station (box present) | Not installed | 17 | EC | Open |  |  | 5
03 | 31 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 5
04 | 1 | CT04LCPA | Install ERP-RTO card + jumper | Missing part |  | EC | Open |  |  | 6
04 | 2 | CT04LCPA | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 6
04 | 3 | CT04LCPA | Run DMX to Level 06 | Cable not run |  | EC | Open |  |  | 6
04 | 4 | CT04LCPA | Terminate DMX to Level 06 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 6
04 | 5 | CT04LCPA | Terminate DMX to Level 03 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 6
04 | 6 | EBDK (CT04LCPA) | Provide sense feed to EBDK | Cable not run | 1 | EC | Open |  |  | 6
04 | 7 | PI1104 S1 - Corridor at Stair A | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring | 2 | EC | Open |  |  | 6
04 | 8 | PI1104 S2 - Corridor near Stair D | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring | 3 | EC | Open |  |  | 6
04 | 9 | PI1002 S7 - Corridor at Pre-Action XX04-3P01 | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring |  | EC | Open |  |  | 6
04 | 10 | PI1002 S8 - Corridor XX04-C013 west | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring |  | EC | Open |  |  | 6
04 | 11 | PI1002 S9 - Corridor XX04-C013 east | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring |  | EC | Open |  |  | 6
04 | 12 | PI1002 S10 - Passage XX04-C010 | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring |  | EC | Open |  |  | 6
04 | 13 | PI1002 S13 - Corridor XX04-C004A | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring | 8 | EC | Open |  |  | 6
04 | 14 | P-DOC-SM2 D5 - Passage XX04-C021 | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring | 11 | EC | Open |  |  | 6
04 | 15 | PI1104 S4 - Consult XX04-1104 wall | Not installed: install box, pull wire, install station | Not installed | 4 | EC | Open |  |  | 6
04 | 16 | PI1002 S6 - Corridor at Pharm XX04-1106 | Not installed: confirm location (empty boxes on opposite wall), pull wire, install station | Not installed | 5 | EC | Open |  |  | 6
04 | 17 | PI1002 S11 - Corridor XX04-C014 | Not installed: install station (box present) | Not installed | 6 | EC | Open |  |  | 6
04 | 18 | PI1002 S12 - Corridor near Elevator Lobby A | Not installed: install box, pull wire, install station | Not installed | 7 | EC | Open |  |  | 6
04 | 19 | PI1002 S14 - Elevator Lobby C XX04-C002 | Not installed: install station (box present) | Not installed | 9 | EC | Open |  |  | 6
04 | 20 | P-DOC-C-LR D1 - Elevator Lobby B XX04-C003 | Not installed: install sensor | Not installed |  | EC | Open |  |  | 6
04 | 21 | P-DOC-C-LR D4 - Elevator Lobby C XX04-C002 | Not installed: install sensor | Not installed | 10 | EC | Open |  |  | 6
04 | 22 | Elec XX04-1E01 | Gain access; survey CT04LCPB, EBDK, P-NSPS-D and Unison terminations | Access |  | ETC | Closed | 2026-10-08 | Updated device list and connections list | 6
04 | 23 | Conf XX04-3108A/B | Gain access; survey UFMP8, UHCI-WM, 2x PI1004, 2x P-DOC-C-LR | Access |  | ETC | Closed | 2026-10-08 | Updated device list and connections list | 6
04 | 24 | PI1104 S3, P-DOC-SM2 D6, P-LS D7 | Check devices | Missed Survey |  | ETC | Closed | 2026-10-08 | Updated in device list | 6
04 | 25 | CT04LCPB | Install ERP-RTO card + jumper | Missing part | 14 | EC | Open |  |  | 6
04 | 26 | CT04LCPB | Land 0-10V control wiring | Termination | 14 | EC | Open |  |  | 6
04 | 27 | CT04LCPB | Terminate DMX to Level 03 | Missing part |  | EC/ETC | Open |  | Waiting on DMX Termination Kits | 6
04 | 28 | CT04LCPB | Identify origin of network run from Level 03 | Information |  | EC | Open |  | 1 net run from Level 03; where does it come from? | 6
04 | 29 | P-NSPS-D - Elec XX04-1E01 | Not installed: install P-NSPS-D and land 120V and Unison wire | Not installed | 14 | EC | Open |  |  | 6
04 | 30 | P-NSPS-D - Elec XX04-1E01 | Terminate network to Level 06 | Termination |  | ETC | Open |  | Hanging outside conduit | 6
04 | 31 | Stations & sensors | Re-pull 2 Unison runs with correct wire type (Belden 8471) | Wiring |  | EC | Open |  | 2 runs outside conduit in Elec XX04-1E01; DMX cable used | 6
04 | 32 | UFMP8 - Conf XX04-3108A/B | Run DMX from Level 06 | Cable not run | 16 | EC | Open |  | Term kit in box | 6
04 | 33 | UHCI-WM - Conf XX04-3108A/B | Not installed: install UHCI-WM | Not installed |  | EC | Open |  |  | 6
04 | 34 | Elec XX04-1E01 | Confirm origin of possible Aux 24V wire next to CT04LCPB | Information |  | EC | Open |  | Hanging outside conduit | 6
04 | 35 | Partition sensors - Conf XX04-3108A/B | Not installed: install partition sensors | Not installed |  | EC | Open |  |  | 6
04 | 36 | PI1104 S3 - Corridor XX04-C026 | Not installed: install box, pull wire, install station | Not installed | 12 | EC | Open |  |  | 6
04 | 37 | PI1004 S15 - Conf XX04-3108B | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring |  | EC | Open |  |  | 6
04 | 38 | PI1004 S16 - Conf XX04-3108A | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring |  | EC | Open |  |  | 6
04 | 39 | P-DOC-C-LR D2 - Conf XX04-3108B | Not installed: install sensor | Not installed | 15 | EC | Open |  |  | 6
04 | 40 | P-DOC-C-LR D3 - Conf XX04-3108A | Not installed: install sensor | Not installed | 15 | EC | Open |  |  | 6
04 | 41 | P-DOC-SM2 D6 - Corridor XX04-C023 at Stair D | Re-pull correct wire type (Belden 8471) and re-terminate with Wagos (provided in box); provide ground | Wiring | 13 | EC | Open |  |  | 6
04 | 42 | P-DOC-SM2 D6 - Corridor XX04-C023 at Stair D | Check sensor, sticky buttons | Missed Survey | 13 | ETC | Open |  |  | 6
04 | 43 | P-LS D7 - Corridor XX04-C028 | Not installed: install sensor | Not installed |  | EC | Open |  | No ceiling | 6
04 | 44 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 6
06 | 13 | PI1002 #2 — Corridor XX06-C006 | Not installed: pull wire, install station (box present) | Not installed | 5 | EC | Open |  |  | 7
06 | 14 | PI1002 #3 — Corridor XX06-C006 | Not installed: install box, pull wire, install station | Not installed | 6 | EC | Open |  |  | 7
06 | 18 | All devices | Missing all Device Neuron IDs | Information |  | EC | Open |  |  | 7
06M | 1 | CT06LCPB | Install ERP-FT-LVD (0-10V card) | Missing part |  | EC | Open |  |  | 8
06M | 2 | CT06LCPB | Run 2x DMX cables to Lvl 9 & 6M Equipment Rack | Cable not run |  | EC | Open |  |  | 8
06M | 3 | Equipment rack | Install 1U brush panel | Missing part |  | EC/ETC | Open |  | ETC waiting on 1U Brush Panel from EC to install | 8
06M | 4 | Equipment rack | Install ERn blank panel | Missing part |  | ETC | Open |  | Could be in a different box? | 8
06M | 5 | Equipment rack | Run DMX to B3B Elev Core C fixture | Cable not run |  | EC | Open |  |  | 8
06M | 6 | Equipment rack | Run DMX to B7 Stair A fixture | Cable not run |  | EC | Open |  |  | 8
06M | 7 | Equipment rack | Run 2x spare DMX (Where?) | Cable not run |  | EC | Open |  |  | 8
06M | 8 | Equipment rack | Run fiber to Equipment rack Level 28 | Cable not run |  | EC | Open |  |  | 8
06M | 9 | Equipment rack | Terminate fiber to Equipment rack Level 01 | Termination |  | EC | Open |  |  | 8
06M | 10 | Equipment rack | Terminate 2x network runs to ERn4 Level 16 | Termination |  | ETC | Open |  |  | 8
06M | 11 | CT06LCPA | Pull second DMX run | Cable not run |  | EC | Open |  | 1 of 2 run to CT06LCPA, Which line is currently run? Lower level? | 8
06M | 12 | CT06LCPA | Terminate DMX | Missing part |  | EC/ETC | Open |  | 1 of 2 run to CT06LCPA, Which line is currently run? Lower level?; ETC Waiting on DMX Termination Kits | 8
06M | 15 | PI1002 stations | Terminate Unison runs at rack | Termination |  | ETC | Open |  | 4 runs pulled | 8
06M | 16 | CT06LCPB | Land 0-10V control wiring | Termination |  | EC | Open |  |  | 8
06M | 17 | Equipment rack | Run 120V to equipment rack | Cable not run |  | EC | Open |  |  | 8

## Missing Parts
Missing Parts
Levels B2-06
Level | # | Device / Location | Part | Part no. | Qty | Owner | Source | Part status | Notes | Floor Order
B2 | 1 | CTB2LCPB | DMX termination kit - Level B1 run |  | 1 | EC | Punch #2 | Needed | Need to be ordered | 1
B2 | 2 | S1 | PI1002 cover |  | 1 | EC | Punch #7 | Needed | Confirm whether on site (provided in box) | 1
B2 | 3 | D1 | P-DOC-C-LR sensor | P-DOC-C-LR | 1 | EC | Punch #8 | Needed | Confirm whether on site | 1
B1 | 1 | CTB1LCPB | ERP-RTO jumper |  | 1 | EC | Punch #1 | Needed | Need to be ordered | 2
B1 | 2 | CTB1LCPB | DMX termination kit - Level 01 run |  | 1 | EC | Punch #4 | Needed | Need to be ordered | 2
B1 | 3 | CTB1LCPB | DMX termination kit - Level B2 run |  | 1 | EC | Punch #5 | Needed | Need to be ordered | 2
B1 | 4 | S3-S9 | PI1002 cover |  | 7 | EC | Punch #8-14 | Needed | Confirm whether on site (provided in box) | 2
B1 | 5 | S1, D3, D4 | Backbox for device |  | 3 | EC | Punch #15, #19, #20 | Needed | Confirm whether on site | 2
B1 | 6 | S1, S2 | PI1002 station | PI1002 | 2 | EC | Punch #15, #16 | Needed | Confirm whether on site | 2
B1 | 7 | D1-D3, D5-D8 | P-DOC-W sensor | P-DOC-W | 7 | EC | Punch #17-19, #21-24 | Needed | Confirm whether on site | 2
B1 | 8 | D4, D13, D14 | P-DOC-C-LR sensor | P-DOC-C-LR | 3 | EC | Punch #20, #25, #26 | Needed | Confirm whether on site | 2
01 | 1 | CT01LCPB | ERP-RTO jumper |  | 1 | EC | Punch #1 | Needed | Need to be ordered | 3
01 | 2 | CT01LCPB, CT01LCPA | ERP-FT-LVD (0-10V card) | ERP-FT-LVD | 2 | EC | Punch #38, #39 | Needed | Need to be ordered | 3
01 | 3 | Equipment rack | 1U brush panel |  | 1 | EC | Punch #7 | Needed | Confirm whether on site | 3
01 | 4 | Equipment rack | Fiber kit part | N2019 | 1 | EC | Punch #8 | Installed | Verified 10/8 | 3
01 | 5 | Equipment rack | Fiber kit part | SGN1253 | 1 | EC | Punch #8 | Installed | Verified 10/8 | 3
01 | 6 | Equipment rack | Fiber kit part | SGM1612 | 1 | EC | Punch #8 | Needed | Need to be ordered | 3
01 | 7 | Equipment rack | Fiber kit part | SGN1021 | 1 | EC | Punch #8 | Needed | Need to be ordered | 3
01 | 8 | Equipment rack | DMX termination kit - B3A Canyon run |  | 1 | EC | Punch #42 | Needed | Need to be ordered | 3
01 | 9 | Equipment rack | DMX termination kit - C13A Oculus run |  | 1 | EC | Punch #43 | Needed | Need to be ordered | 3
01 | 10 | Equipment rack | DMX termination kit - D1 ED Column Capital run |  | 1 | EC | Punch #44 | Needed | Need to be ordered | 3
01 | 11 | Equipment rack | DMX termination kit - UFMP4 run |  | 1 | EC | Punch #45 | Needed | Need to be ordered | 3
01 | 12 | Info Desk WT01-1046 | P-TS7-E 7in touchscreen | P-TS7-E | 1 | EC | Punch #10 | Needed | Confirm whether on site | 3
01 | 13 | Vest WT01-1044, BH OBS 47, 48 | Foundry UFMP4 | UFMP4 | 3 | EC | Punch #11-13 | Needed | Confirm whether on site | 3
01 | 14 | BH OBS 49, 50, 51, 52 | Foundry UFMP4 | UFMP4 | 4 | EC | Punch #14-17 | On site | On site above ceiling; needs to be installed | 3
01 | 15 | S5 | Backbox for station |  | 1 | EC | Punch #22 | Needed | Confirm whether on site | 3
01 | 16 | S5, S7-S14, S20, S22 | PI1104 station | PI1104 | 11 | EC | Punch #22-28, #30, #31, #33, #52 | Needed | Confirm whether on site | 3
01 | 17 | S16, S18 | PI1004 station | PI1004 | 2 | EC | Punch #32, #51 | Needed | Confirm whether on site | 3
01 | 18 | D1 | P-DOC-C-LR sensor | P-DOC-C-LR | 1 | EC | Punch #34 | Needed | Confirm whether on site | 3
01 | 19 | Equipment rack | DMX termination kit - CT01LCPB run |  | 1 | EC | Punch #40 | Needed | Need to be ordered | 3
01 | 20 | Equipment rack | DMX termination kit - CT01LCPA run |  | 1 | EC | Punch #41 | Needed | Need to be ordered | 3
02 | 1 | CT02LCPA | DMX termination kit - Level 03 run |  | 1 | EC | Punch #4 | Needed | Need to be ordered | 4
02 | 2 | CT02LCPA | DMX termination kit - Level 01 run |  | 1 | EC | Punch #5 | Needed | Need to be ordered | 4
02 | 3 | CT02LCPB | DMX termination kit - Level 03 run |  | 1 | EC | Punch #9 | Needed | Need to be ordered | 4
02 | 4 | CT02LCPB | DMX termination kit - UFMP4 run |  | 1 | EC | Punch #10 | Needed | Need to be ordered | 4
02 | 5 | Elec XX02-1E01 | P-NSPS-D-KIT | P-NSPS-D-KIT | 1 | EC | Punch #7 | Needed | Confirm whether on site | 4
02 | 6 | Elec XX02-1E02 | Foundry UFMP4 | UFMP4 | 1 | EC | Punch #12 | Needed | Confirm whether on site | 4
02 | 7 | S1, S5, S11, S13, S14, S15 | PI1002 station | PI1002 | 6 | EC | Punch #15, #16, #18, #19, #30, #31 | Needed | Confirm whether on site | 4
02 | 8 | S12 | PI1104 station | PI1104 | 1 | EC | Punch #17 | Needed | Confirm whether on site | 4
02 | 9 | D1, D4, D10, D11, D23, D24 | P-DOC-C-LR sensor | P-DOC-C-LR | 6 | EC | Punch #20, #21, #23-26 | Needed | Confirm whether on site | 4
02 | 10 | S11, S15 | Backbox for station |  | 2 | EC | Punch #30, #31 | Needed | Confirm whether on site | 4
03 | 1 | CT03LCPA | I/O card |  | 1 | EC | Punch #1 | Needed | Part number to follow; need to be ordered | 5
03 | 2 | CT03LCPA | DMX termination kit - UFMP4 run |  | 1 | EC | Punch #3 | Needed | Need to be ordered | 5
03 | 3 | CT03LCPA | DMX termination kit - Level 02 run |  | 1 | EC | Punch #4 | Needed | Need to be ordered | 5
03 | 4 | CT03LCPB | DMX termination kit - Level 04 run |  | 1 | EC | Punch #7 | Needed | Need to be ordered | 5
03 | 5 | CT03LCPB | DMX termination kit - Level 02 run |  | 1 | EC | Punch #8 | Needed | Need to be ordered | 5
03 | 6 | UFMP4 #1 | DMX termination kit - CT03LCPA or Level 04 run |  | 1 | EC | Punch #10 | Needed | Need to be ordered | 5
03 | 7 | UFMP4 #2 | DMX termination kit - CT03LCPA or Level 04 run |  | 1 | EC | Punch #11 | Needed | Need to be ordered | 5
03 | 8 | S4, S9 | PI1104 cover |  | 2 | EC | Punch #13, #15 | Needed | Confirm whether on site (provided in box) | 5
03 | 9 | D2 | P-DOC-C-LR cover |  | 1 | EC | Punch #16 | Needed | Confirm whether on site (provided in box) | 5
03 | 10 | S6 | PI1104 station (replacement) | PI1104 | 1 | EC | Punch #14 | Needed | Need to be ordered | 5
03 | 11 | S8 | PI1104 station | PI1104 | 1 | EC | Punch #17 | Needed | Confirm whether on site | 5
03 | 12 | S11, S12, S13, S15, S16, S18 | PI1002 station | PI1002 | 6 | EC | Punch #18-21, #29, #30 | Needed | Confirm whether on site | 5
03 | 13 | D4, D8, D9 | P-DOC-C-LR sensor | P-DOC-C-LR | 3 | EC | Punch #22-24 | Needed | Confirm whether on site | 5
03 | 14 | D10 | P-LS sensor | P-LS | 1 | EC | Punch #25 | Needed | Confirm whether on site | 5
03 | 15 | UFMP4 #1 | DMX termination kit - missing run |  | 1 | EC | Punch #27 | Needed | Need to be ordered | 5
03 | 16 | UFMP4 #2 | DMX termination kit - missing run |  | 1 | EC | Punch #28 | Needed | Need to be ordered | 5
04 | 1 | CT04LCPA, CT04LCPB | ERP-RTO card + jumper | ERP-RTO | 2 | EC | Punch #1, #25 | Needed | Need to be ordered | 6
04 | 2 | CT04LCPA | DMX termination kit - Level 06 run |  | 1 | EC | Punch #3, #4 | Needed | Need to be ordered | 6
04 | 3 | CT04LCPA | DMX termination kit - Level 03 run |  | 1 | EC | Punch #5 | Needed | Need to be ordered | 6
04 | 4 | CT04LCPB | DMX termination kit - Level 03 run |  | 1 | EC | Punch #27 | Needed | Need to be ordered | 6
04 | 5 | UFMP8 | DMX termination kit - Level 06 run |  | 1 | EC | Punch #32 | On site | Term kit in box | 6
04 | 6 | S3, S4, S12 | Backbox for station |  | 3 | EC | Punch #15, #18, #36 | Needed | Confirm whether on site | 6
04 | 7 | S3, S4 | PI1104 station | PI1104 | 2 | EC | Punch #15, #36 | Needed | Confirm whether on site | 6
04 | 8 | S6, S11, S12, S14 | PI1002 station | PI1002 | 4 | EC | Punch #16-19 | Needed | Confirm whether on site | 6
04 | 9 | D1, D2, D3, D4 | P-DOC-C-LR sensor | P-DOC-C-LR | 4 | EC | Punch #20, #21, #39, #40 | Needed | Confirm whether on site | 6
04 | 10 | Elec XX04-1E01 | P-NSPS-D-KIT | P-NSPS-D-KIT | 1 | EC | Punch #29 | Needed | Confirm whether on site | 6
04 | 11 | Conf XX04-3108A/B | UHCI-WM partition sensor | UHCI-WM | 1 | EC | Punch #33 | Needed | Confirm whether on site | 6
04 | 12 | Conf XX04-3108A/B | Partition sensors |  |  | EC | Punch #35 | Needed | Confirm whether on site | 6
04 | 13 | D7 | P-LS sensor | P-LS | 1 | EC | Punch #43 | Needed | Confirm whether on site | 6
06 | 14 | PI1002 #3 - Corridor XX06-C006 | Backbox for station |  | 1 | EC | Punch #14; Devices 06-S3 | Needed | Confirm whether on site | 7
06 | 15 | PI1002 #2 / #3 - Corridor XX06-C006 | PI1002 station | PI1002 | 2 | EC | Punch #13, #14 | Needed | Not installed; confirm whether devices are on site | 7
06M | 1 | CT06LCPB | ERP-FT-LVD (0-10V card) | ERP-FT-LVD | 1 | EC | Punch #1; Devices 06M-02 | Needed | Confirm whether on site | 8
06M | 2 | Equipment rack | 1U brush panel |  | 1 | EC | Punch #3; Devices 06M-01 | Needed | Confirm whether on site | 8
06M | 3 | Equipment rack | ERn blank panel |  | 1 | EC | Punch #4; Devices 06M-01 | Needed | Confirm whether on site | 8
06M | 4 | Equipment rack | DMX termination kit - B3B Elev Core C fixture run |  | 1 | EC | Punch #5 | Needed | Need to be ordered | 8
06M | 5 | Equipment rack | DMX termination kit - B7 Stair A fixture run |  | 1 | EC | Punch #6 | Needed | Need to be ordered | 8
06M | 6 | Equipment rack | DMX termination kit - spare DMX out runs |  | 2 | EC | Punch #7 | Needed | Need to be ordered | 8
06M | 7 | Equipment rack | Fiber kit part | SGN1253 | 1 | EC | Connections C-06 (fiber to Level 01) | Needed | Need to be ordered | 8
06M | 8 | Equipment rack | Fiber kit part | SGM1612 | 1 | EC | Connections C-06 (fiber to Level 01) | Needed | Need to be ordered | 8
06M | 9 | Equipment rack | Fiber kit part | SGN1021 | 1 | EC | Connections C-06 (fiber to Level 01) | Needed | Need to be ordered | 8
06M | 10 | CT06LCPB | DMX termination kit - Level 09 run |  | 1 | EC | Punch #2 | Needed | Need to be ordered | 8
06M | 11 | CT06LCPB | DMX termination kit - 6M Equipment Rack run |  | 1 | EC | Punch #2 | Needed | Need to be ordered | 8
06M | 12 | CT06LCPA | DMX termination kit - Level 09 run |  | 1 | EC | Punch #11, #12 | Needed | Need to be ordered | 8
06M | 13 | CT06LCPA | DMX termination kit - Level 04 run |  | 1 | EC | Punch #11, #12 | Needed | Need to be ordered | 8

## Photo Log
Photo Log
Levels B2-06
Level | Photo | Location | Subject | What it shows | Device ID | Floor Order | Image
B2 | 1 | Elec XXB2-2E02 | CTB2LCPB - wires in ERP | Relay panel open; network and Unison wires land in ERP. | B2-01 | 1
B2 | 2 | Elec XXB2-2E02 | P-NSPS-D - 48V jumper | NSPS in enclosure; 48V jumper from power supply not landed. | B2-03 | 1
B2 | 3 | Elevator Lobby B XXB2-C003 | PI1002 S1 - missing cover | Station on conduit box; no cover. | B2-S1 | 1
B2 | 4 | Elevator Lobby B XXB2-C003 | P-DOC-C-LR D1 - NI | Conduit box open at ceiling; no device. | B2-D1 | 1
B1 | 1 | Elec WTB1-1E01 | CTB1LCPB / EBDK - moved | Relay panel and EBDK in new location. | B1-01, B1-02 | 2
B1 | 2 | Corridor XXB1-C009 | P-DOC-W D1 - NI | Box on conduit; no sensor. | B1-D1 | 2
B1 | 3 | Corridor XXB1-C009 at Fan Room XXB1-2F01 | P-DOC-W D2 - NI | Box on conduit; no sensor. | B1-D2 | 2
B1 | 4 | Corridor XXB1-C007 at Stair F XXB1-3S02 | PI1002 S2 - NI | Box present with wire; no station. | B1-S2 | 2
B1 | 5 | Corridor XXB1-C007 | P-DOC-W D5 - NI | Empty box on wall. | B1-D5 | 2
B1 | 6 | Corridor XXB1-C007 at Confident Waste XXB1-3017 | P-DOC-W D6 - NI | Empty box on wall. | B1-D6 | 2
B1 | 7 | Corridor XXB1-C006 at Cart Wash XXB1-3007 | P-DOC-W D7 - NI | Empty box on wall. | B1-D7 | 2
B1 | 8 | Corridor XXB1-C006 at Trash Compactor XXB1-2TC01 | P-DOC-W D8 - NI | Empty box on wall. | B1-D8 | 2
B1 | 9 | Corridor XXB1-C005 | PI1002 S3 - spot check | Spot check: box opened, Wire good, Wago terminations. Reinstalled. | B1-S3 | 2
B1 | 10 | Corridor XXB1-C005 | PI1002 S3 - missing cover | Station reinstalled; no cover. | B1-S3 | 2
B1 | 11 | Corridor XXB1-C005 | PI1002 S4 - missing cover | Station installed; no cover. | B1-S4 | 2
B1 | 12 | Corridor XXB1-C008 | P-DOC-C-LR D13 - NI | Open ceiling at sensor location. Looks like unison wire. | B1-D13 | 2
01 | 1 | Hydra XX01-3137 | PI1104 S15 - wire nuts | Station hanging below red button; wire nuts. | 01-S15 | 3
01 | 2 | Corridor XX01-C004 | PI1002 S19 - wire nuts | Station hanging from box; wire nuts. | 01-S19 | 3
01 | 3 | Corridor XX01-C015 | PI1004 S16 - NI | Blank plate on box beside card reader. | 01-S16 | 3
01 | 4 | ALC. HW WT01-C024A | PI1104 S13 - NI | Box present with wire. | 01-S13 | 3
01 | 5 | BH OBS RM 49 WT01-2008 | UFMP4 - NI | UFMP4 unit sitting above ceiling. | 01-10 | 3
01 | 6 | Passageway WT01-C022 (BH OBS) | PI1104 S8-S12 - 3-gang box | 3-gang box installed for 1-gang switch. | 01-S8 to 01-S12 | 3
01 | 7 | Passageway WT01-C023 | PI1104 S14 - NI | Box present with wire. | 01-S14 | 3
01 | 8 | Tlt. Pat Stf WT01-2161 | PI1104 S22 - NI | Empty box with wire beside red button. | 01-S22 | 3
01 | 9 | Info Desk WT01-1046 | PI1104 S5 - NI, no box | Box present with wire. | 01-S5 | 3
01 | 10 | NS WT01-2101 | PI1104 S20 - NI | Box installed with wire; no ground; no station. | 01-S20 | 3
01 | 11 | SLD HLD WT01-2001 | PI1004 S18 - NI | Box installed with wire; no ground; no station. | 01-S18 | 3
01 | 12 | Elec WT01-1E02 | Equipment rack - wall section | Wall section open; incoming runs coiled; 120V box not secured. | 01-05 | 3
01 | 13 | Elec WT01-1E02 | Equipment rack - front | Rack front with control processors, switch and UPS. | 01-05 | 3
01 | 14 | Elec XX01-1E02 | CT01LCPB open | Panel open; 0-10V wiring run, not landed. | 01-01 | 3
01 | 15 | Elec XX01-1E01 | CT01LCPA and EBDK | Panel open; 0-10V wiring run, not terminated; EBDK beside panel. | 01-03, 01-04 | 3
02 | 1 | Elec XX02-1E02 | CT02LCPB circuit list | Handwritten circuit list on panel door. | 02-04 | 4
02 | 2 | Corridor at Tlt. Stf XX02-1020 | PI1002 S9 - spot check | Wagos used like wire nuts, wire stripped too long; re-terminated on site, device good. | 02-S9 | 4
02 | 3 | Corridor XX02-C010 | P-DOC-C-LR D4 - NI | Ceiling at drawn location; installed sensor appears to be a Wattstopper, confirm. | 02-D4 | 4
02 | 4 | Elevator Lobby A XX02-C001 | PI1002 S11 - NI, no box | Elevator lobby wall at drawn location; no box. | 02-S11 | 4
02 | 5 | Elec XX02-1E02 | CT02LCPB and EBDK | Panel open; EBDK below. | 02-04, 02-05 | 4
02 | 6 | Elec XX02-1E01 | CT02LCPA and EBDK | Panel open; 0-10V wiring run, not terminated; EBDK below. | 02-01, 02-02 | 4
03 | 1 | Elec XX03-1E01 | CT03LCPA open | Panel open; control board, 0-10V and network wiring exposed. | 03-01 | 5
03 | 2 | Elec XX03-1E01 | EBDK (CT03LCPA) | EBDK keyed, closed. | 03-02 | 5
03 | 3 | Elec XX03-1E04 | CT03LCPB open | Panel open; 120v wire run, not landed. Net run not term. | 03-03 | 5
03 | 4 | Elec XX03-1E04 | CT03LCPB wall | Panel between electrical cabinets | 03-03 | 5
03 | 5 | Semi-Restr Corridor XX03-C028 | PI1104 S4 - missing cover | Station installed, cover missing. | 03-S4 | 5
03 | 6 | Frozen Section XX03-1106 door | PI1104 S5 - spot check | Box opened to inspect wiring; device reinstalled afterward. | 03-S5 | 5
03 | 7 | ALC. Stretcher XX03-2094 | PI1104 S6 - trim cut | Station left trim cut. Borken top trim; Station broken; needs replacement. | 03-S6 | 5
03 | 8 | ALC. Stretcher XX03-2094 | PI1104 S6 - broken | Broken station opened to inspect wiring; Wireing is good. device NOT reinstalled afterward to be replaced. | 03-S6 | 5
03 | 9 | Corridor XX03-C014A | PI1104 S8 - NI | Boxes present, no station. | 03-S8 | 5
03 | 10 | Reception / Info Desk XX03-2102 | PI1104 S9 - missing cover | Station installed, cover missing. | 03-S9 | 5
03 | 11 | ALC. HW XX03-3109 | PI1104 S10 | Box open beside red button; installed, untested. | 03-S10 | 5
03 | 12 | Elevator Lobby B XX03-C003 | PI1002 S13 - NI | Box present, no station. | 03-S13 | 5
03 | 13 | OR (Stat) Lab XX03-1108 | P-DOC-C-LR D2 - missing cover | Sensor in ceiling, cover missing. | 03-D2 | 5
03 | 14 | Corridor XX03-C014A | P-DOC-C-LR D8 - NI | Wire hanging at ceiling; no sensor. | 03-D8 | 5
03 | 15 | Semi-Restr Corridor XX03-C028 | UFMP4 #1, #2 | Both UFMP4s on wall at ceiling; one DMX run to each. | 03-06, 03-07 | 5
03 | 16 | Corridor XX03-C014 | PI1002 S15 - NI | Box present, no station. | 03-S15 | 5
03 | 17 | Corridor XX03-C014 | PI1002 S16 - NI | Box present beside elevator, no station. | 03-S16 | 5
04 | 1 | Elec XX04-1E04 | CT04LCPA and EBDK | Panel open, control board and 0-10V wiring exposed; EBDK below. | 04-01, 04-02 | 6
04 | 2 | Corridor at Stair A XX04-2S01 | PI1104 S1 - wire nuts | Station hanging from box; wire nuts on wrong wire type. | 04-S1 | 6
04 | 3 | Corridor near Stair D XX04-3S03 | PI1104 S2 - wire nuts | Station installed; wrong wire type visible at box edge. | 04-S2 | 6
04 | 4 | Consult XX04-1104 wall | PI1104 S4 - NI, no box | Column at drawn location; no box. | 04-S4 | 6
04 | 5 | Corridor at Pharm XX04-1106 | PI1002 S6 - NI, location | Nothing at drawn location; empty boxes on opposite wall. | 04-S6 | 6
04 | 6 | Corridor XX04-C014 | PI1002 S11 - NI | Box present, no station. | 04-S11 | 6
04 | 7 | Corridor near Elevator Lobby A | PI1002 S12 - NI, no box | Wall under construction behind scaffold. | 04-S12 | 6
04 | 8 | Corridor XX04-C004A | PI1002 S13 - wire nuts, no ground | Wire nuts, wrong wire type; DMX conductor used as ground. | 04-S13 | 6
04 | 9 | Elevator Lobby C XX04-C002 | PI1002 S14 - NI | Box present, no station. | 04-S14 | 6
04 | 10 | Elevator Lobby C XX04-C002 | P-DOC-C-LR D4 - NI | Ceiling grid open; no sensor. | 04-D4 | 6
04 | 11 | Passage XX04-C021 | P-DOC-SM2 D5 - wire nuts | Wire nuts on wrong wire type. | 04-D5 | 6
04 | 12 | Corridor XX04-C026 | PI1104 S3 - NI, no box | Wall at drawn location; no box. | 04-S3 | 6
04 | 13 | Corridor XX04-C023 at Stair D XX04-3S03 | P-DOC-SM2 D6 - wire nuts | Sensor hanging from box; wire nuts on wrong wire type. | 04-D6 | 6
04 | 14 | Elec XX04-1E01 | CT04LCPB, EBDK and P-NSPS-D location | Panel open; EBDK beside panel; runs hanging outside conduit. | 04-03, 04-04, 04-05 | 6
04 | 15 | Conf XX04-3108A/B | P-DOC-C-LR D2, D3 - NI | Conference room ceiling; no P-DOC-C-LR installed. | 04-D2, 04-D3 | 6
04 | 16 | Conf XX04-3108A/B | UFMP8 - no DMX | UFMP8 installed above ceiling; loads landed, no DMX. | 04-06 | 6
06 | 4 | Corridor XX06-C007 at Shaft 1 door | PI1002 #1 spot check | Box opened to inspect splices; device reinstalled afterward. | 06-S1 | 7
06 | 5 | Corridor XX06-C006 (r6f) | PI1002 #2 — NI, no wire | Backbox present with stainless blank plate; no wire. | 06-S2 | 7
06 | 6 | Corridor XX06-C006 (6g) | PI1002 #3 — NI, no box | Bare wall at the drawn location; no box. | 06-S3 | 7
06M | 1 | Stair A Vestibule area | Equipment rack open + CT06LCPB open | Swing rack front section open, wall section with coiled cable and quad receptacle; CT06LCPB door open with board exposed; EBDK below. | 06M-01, 06M-02 | 8
06M | 2 | Stair A Vestibule area | Equipment rack front | P-SPM-E, 2x P-ACP, 24-port patch panel, Cisco PoE switch, Response Mk2 gateway, blank, UPS. Brush panel and ERn blank not present. | 06M-01 | 8
06M | 3 | Below CT06LCPB | EBDK | Emergency Bypass Detection Kit, keyed, complete. | 06M-03 | 8

## Change Log
Change Log
Levels B2-06
Date | Level | Sheet | Ref | Entry | Field | Was | Now | Change | Reason | Floor Order
2026-10-08 | 01 | Devices | 01-01 | CT01LCPB - Elec XX01-1E02 | Notes | Missing 1x ERP-RTO jumper, 1x ERP-FT-LVD (0-10V card). 0-10V not landed. | Missing 1x ERP-RTO jumper, 1x ERP-FT-LVD (0-10V card). 0-10V not landed. MSS 10/1 shows LVD installed; confirm. | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Devices | 01-03 | CT01LCPA - Elec XX01-1E01 | Notes | Missing 1x ERP-FT-LVD (0-10V card). 0-10V not landed. | Missing 1x ERP-FT-LVD (0-10V card). 0-10V not landed. MSS 10/1 shows LVD installed; confirm. | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Devices | 01-04 | EBDK - Elec XX01-1E01 | Notes | Missing sense feed. | Missing sense feed. MSS 10/1 shows landed; confirm. | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Item | Install ERP-FT-LVD (0-10V card) | Confirm ERP-FT-LVD (0-10V card) is installed | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Type | Missing part | Missed Survey | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Owner | EC | ETC | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Notes |  | MSS 10/1 shows installed; found missing 10/7 | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Item | Install ERP-FT-LVD (0-10V card) | Confirm ERP-FT-LVD (0-10V card) is installed | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Type | Missing part | Missed Survey | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Owner | EC | ETC | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Notes |  | MSS 10/1 shows installed; found missing 10/7 | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Item | Provide sense feed to EBDK | Check sense feed to EBDK | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Type | Cable not run | Missed Survey | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Owner | EC | ETC | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Notes |  | MSS 10/1 shows landed; found missing 10/7 | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 01 | Missing Parts | #2 | CT01LCPB, CT01LCPA - ERP-FT-LVD (0-10V card) | Notes | Confirm whether on site | MSS 10/1 shows installed; confirm on site | MSS ruling | MSS cross-check ruling | 3
2026-10-08 | 02 | Devices | 02-01 | CT02LCPA - Elec XX02-1E01 | Notes | 0-10V not landed. 2 DMX runs to terminate; one DMX wire missing (Level 03 or Level 01, undetermined). | 0-10V not landed. 2 DMX runs to terminate; one DMX wire missing (Level 03 or Level 01, undetermined). (2) 0-10V headers noted missing on MSS 10/1; confirm. | MSS ruling | MSS cross-check ruling | 4
2026-10-08 | 02 | Punch List | #29 | All devices - Missing all Device Neuron IDs | # | 28 | 29 | MSS ruling | Renumbered after an item was inserted | 4
2026-10-08 | 02 | Punch List | #2-#27 | Items after an inserted item | # | #2-#27 | #3-#28 | MSS ruling | Renumbered after an item was inserted | 4
2026-10-08 | 02 | Missing Parts | #1-#9 | Source references | Source | Punch numbers before the MSS check item | Same items, renumbered (+1) | MSS ruling | Renumbered after an item was inserted | 4
2026-10-08 | 01 | Devices | 01-01 | CT01LCPB - Elec XX01-1E02 | Notes | Missing 1x ERP-RTO jumper, 1x ERP-FT-LVD (0-10V card). 0-10V not landed. MSS 10/1 shows LVD installed; confirm. | Missing 1x ERP-RTO jumper, 1x ERP-FT-LVD (0-10V card). 0-10V not landed. | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-01 | CT01LCPB - Elec XX01-1E02 | Photo |  | 14 | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-03 | CT01LCPA - Elec XX01-1E01 | Notes | Missing 1x ERP-FT-LVD (0-10V card). 0-10V not landed. MSS 10/1 shows LVD installed; confirm. | Missing 1x ERP-FT-LVD (0-10V card). 0-10V run, not terminated | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-03 | CT01LCPA - Elec XX01-1E01 | Photo |  | 15 | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-04 | EBDK - Elec XX01-1E01 | Status | Issue | Installed, untested | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-04 | EBDK - Elec XX01-1E01 | Notes | Missing sense feed. MSS 10/1 shows landed; confirm. |  | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-04 | EBDK - Elec XX01-1E01 | Photo |  | 15 | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-05 | Equipment Rack 18U - Elec WT01-1E02 | Notes | Missing 1x 1U brush panel, 1x SFP (N2019). Outgoing runs not surveyed. | Missing 1x 1U brush panel, 1x SGM1612 & SGN1021). Run to rack: 3 DMX, 2 net, 1 ground, 1 fiber, 120v run and terminated but box not secured | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-05 | Equipment Rack 18U - Elec WT01-1E02 | Photo |  | 12,13 | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S6 | PI1002 - Humidifier Closet WT01-2033 | Notes | Locked. | Blocked | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S18 | PI1004 - SLD HLD WT01-2001 | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S18 | PI1004 - SLD HLD WT01-2001 | Notes | Unchecked. | Not installed, box installed, wire present, no ground. | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S18 | PI1004 - SLD HLD WT01-2001 | Photo |  | 11 | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S20 | PI1104 - NS WT01-2101 | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S20 | PI1104 - NS WT01-2101 | Notes | Unchecked. | Not installed, box installed, wire present, no ground. | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S20 | PI1104 - NS WT01-2101 | Photo |  | 10 | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S21 | PI1002 - Passage XX01-C005A / Tlt. Pat XX01-3116T | Status | No access | Installed, untested | Field survey | Field update | 3
2026-10-08 | 01 | Devices | 01-S21 | PI1002 - Passage XX01-C005A / Tlt. Pat XX01-3116T | Notes | Locked. |  | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-03 | CT01LCPB 0-10V Control wiring | Note | Not landed | Run, not terminated | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-07 | CT01LCPA 0-10V Control wiring | Note | Not landed | Run, not terminated | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-09 | Equipment rack X DMX to B3A Canyon | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-09 | Equipment rack X DMX to B3A Canyon | Note | Not surveyed; no term kit | One DMX wire at equipment rack unidentified. Could be this?; no term kit | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-10 | Equipment rack X DMX to C13A Oculus | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-10 | Equipment rack X DMX to C13A Oculus | Note | Not surveyed; no term kit | One DMX wire at equipment rack unidentified. Could be this?; no term kit | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-11 | Equipment rack X DMX to D1 ED Column Capital | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-11 | Equipment rack X DMX to D1 ED Column Capital | Note | Not surveyed; no term kit | One DMX wire at equipment rack unidentified. Could be this?; no term kit | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-12 | Equipment rack X DMX to UFMP4 (7) | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-12 | Equipment rack X DMX to UFMP4 (7) | Note | Not surveyed; no term kit; UFMP4s not installed | One DMX wire at equipment rack unidentified. Could be this?; no term kit | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-13 | Equipment rack N Walter Tower ETC P-CCS | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-13 | Equipment rack N Walter Tower ETC P-CCS | Note | Not surveyed | Not installed, Walter tower conduit empty | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-14 | Equipment rack N Level 02 | Status | No access | Issue | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-14 | Equipment rack N Level 02 | Note | Not surveyed | Net run, not terminated; destination might be wrong room | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-15 | Equipment rack F Equipment rack Level 06 | Status | No access | Issue | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-15 | Equipment rack F Equipment rack Level 06 | Note | Not surveyed; missing kit parts SGN1253, SGM1612, SGN1021, N2019 | Fiber terminated; missing kit parts SGM1612, SGN1021 | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-16 | Equipment rack NG P-TS7-E touchscreen | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-16 | Equipment rack NG P-TS7-E touchscreen | Note | Not surveyed; P-TS7-E not installed | P-TS7-E not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-17 | Stations & sensor U Devices to equipment rack | Status | No access | Not installed | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-17 | Stations & sensor U Devices to equipment rack | Note | Not surveyed at devices | No unison wire at equipment rack | Field survey | Field update | 3
2026-10-08 | 01 | Connections | C-18 | Equipment rack X DMX to CT01LCPB | (row added) |  | Issue | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Connections | C-19 | Equipment rack X DMX to CT01LCPA | (row added) |  | Issue | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Photo |  | 14 | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Tracking status | Open | Closed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Notes | MSS 10/1 shows installed; found missing 10/7 | Needs 2x 0-10v cards, only one installed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Tracking status | Open | Closed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Notes | MSS 10/1 shows installed; found missing 10/7 | Needs 2x 0-10v cards, only one installed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Tracking status | Open | Closed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Notes | MSS 10/1 shows landed; found missing 10/7 | Terminated | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #8 | Equipment rack - Terminate fiber to Equipment rack Level 06 | Tracking status | Open | In progress | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #8 | Equipment rack - Terminate fiber to Equipment rack Level 06 | Notes | Missing kit parts SGN1253, SGM1612, SGN1021, N2019 (SFP) | Fiber terminated in equipment rack; Missing kit parts SGN1021, N2019 (SFP) | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #9 | Equipment rack - Survey outgoing runs (DMX x4, network x2, fiber, NG) and check Unison wiring at each device | Tracking status | Open | Closed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #9 | Equipment rack - Survey outgoing runs (DMX x4, network x2, fiber, NG) and check Unison wiring at each device | Notes | Not surveyed; wire not checked at devices on this level unless marked | Connections list updated | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #35 | PI1002 S6 - Humidifier Closet WT01-2033 - Check device | Notes | Locked | Blocked | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #36 | PI1002 S21 - Passage XX01-C005A - Check device | Tracking status | Open | Closed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #36 | PI1002 S21 - Passage XX01-C005A - Check device | Notes | Locked | Device list updated | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #37 | PI1004 S18, PI1104 S20 - Check devices | Tracking status | Open | Closed | Field survey | Field update | 3
2026-10-08 | 01 | Punch List | #37 | PI1004 S18, PI1104 S20 - Check devices | Notes | Unchecked | Device list updated | Field survey | Field update | 3
2026-10-08 | 01 | Photo Log | Photo 10 | PI1104 S20 - NI | (row added) |  | Box installed with wire; no ground; no station. | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Photo Log | Photo 11 | PI1004 S18 - NI | (row added) |  | Box installed with wire; no ground; no station. | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Photo Log | Photo 12 | Equipment rack - wall section | (row added) |  | Wall section open; incoming runs coiled; 120V box not secured. | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Photo Log | Photo 13 | Equipment rack - front | (row added) |  | Rack front with control processors, switch and UPS. | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Photo Log | Photo 14 | CT01LCPB open | (row added) |  | Panel open; 0-10V wiring run, not landed. | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 01 | Photo Log | Photo 15 | CT01LCPA and EBDK | (row added) |  | Panel open; 0-10V wiring run, not terminated; EBDK beside panel. | Field survey | Added in the 10/8 survey | 3
2026-10-08 | 02 | Devices | 02-01 | CT02LCPA - Elec XX02-1E01 | Notes | 0-10V not landed. 2 DMX runs to terminate; one DMX wire missing (Level 03 or Level 01, undetermined). (2) 0-10V headers noted missing on MSS 10/1; confirm. | 0-10V run not terminated, one DMX run not terminated, one DMX missing (unknown which) | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-01 | CT02LCPA - Elec XX02-1E01 | Photo |  | 6 | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-02 | EBDK - Elec XX02-1E01 | Photo |  | 6 | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-03 | P-NSPS-D-KIT - Elec XX02-1E01 | Notes | Not Installed. | Not Installed. No unison wire in Elec XX-2-1E01 | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-04 | CT02LCPB - Elec XX02-1E02 | Notes | 0-10V not landed. 2 DMX runs to terminate. | 0-10V not run. 2 DMX runs to terminate; 1 net run from lvl 1 for what? | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-04 | CT02LCPB - Elec XX02-1E02 | Photo | 1 | 1,5 | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-05 | EBDK - Elec XX02-1E02 | Status | Issue | Installed, untested | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-05 | EBDK - Elec XX02-1E02 | Notes | Missing sense feed. |  | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-05 | EBDK - Elec XX02-1E02 | Photo |  | 5 | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-S11 | PI1002 - Elevator Lobby A XX02-C001 | Status | No access | Not installed | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-S11 | PI1002 - Elevator Lobby A XX02-C001 | Notes | Not reached. | Not installed, no box | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-S11 | PI1002 - Elevator Lobby A XX02-C001 | Photo |  | 4 | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-S15 | PI1002 - East corridor south of Seating XX02-C016 | Status | No access | Not installed | Field survey | Field update | 4
2026-10-08 | 02 | Devices | 02-S15 | PI1002 - East corridor south of Seating XX02-C016 | Notes | Inaccessible. | Not installed, no box | Field survey | Field update | 4
2026-10-08 | 02 | Connections | C-07 | CT02LCPB 0-10V Control wiring | Status | Issue | Not installed | Field survey | Field update | 4
2026-10-08 | 02 | Connections | C-07 | CT02LCPB 0-10V Control wiring | Note | Not landed | Not run | Field survey | Field update | 4
2026-10-08 | 02 | Connections | C-09 | Stations & sensors U Devices to P-NSPS-D | Note | Not run; P-NSPS-D not installed | Not run; P-NSPS-D not installed; have not found unison wire location | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #2 | CT02LCPA - Check (2) 0-10V headers | Photo |  | 5 | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #2 | CT02LCPA - Check (2) 0-10V headers | Tracking status | Open | Closed | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #2 | CT02LCPA - Check (2) 0-10V headers | Notes | MSS 10/1 noted headers missing; not observed 10/7, assumed in place | Headers installed | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #11 | EBDK (CT02LCPB) - Provide sense feed to EBDK | Tracking status | Open | Closed | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #11 | EBDK (CT02LCPB) - Provide sense feed to EBDK | Notes |  | Sense run and terminated | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #27 | PI1002 S11 - Elevator Lobby A XX02-C001 - Check device | Tracking status | Open | Closed | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #27 | PI1002 S11 - Elevator Lobby A XX02-C001 - Check device | Notes |  | Updated device list. | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #28 | PI1002 S15 - East corridor south of Seating - Check device | Tracking status | Open | Closed | Field survey | Field update | 4
2026-10-08 | 02 | Punch List | #28 | PI1002 S15 - East corridor south of Seating - Check device | Notes | Inaccessible | Updated device list. | Field survey | Field update | 4
2026-10-08 | 02 | Photo Log | Photo 4 | PI1002 S11 - NI, no box | (row added) |  | Elevator lobby wall at drawn location; no box. | Field survey | Added in the 10/8 survey | 4
2026-10-08 | 02 | Photo Log | Photo 5 | CT02LCPB and EBDK | (row added) |  | Panel open; EBDK below. | Field survey | Added in the 10/8 survey | 4
2026-10-08 | 02 | Photo Log | Photo 6 | CT02LCPA and EBDK | (row added) |  | Panel open; 0-10V wiring run, not terminated; EBDK below. | Field survey | Added in the 10/8 survey | 4
2026-10-08 | 03 | Devices | 03-06 | UFMP4 - Semi-Restr Corridor XX03-C028 | Notes | DMX run, not terminated; need DMX term kit. | DMX run, not terminated; need DMX term kit. Missing one DMX cable, which is missing? | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-06 | UFMP4 - Semi-Restr Corridor XX03-C028 | Photo |  | 15 | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-07 | UFMP4 - Semi-Restr Corridor XX03-C028 | Notes | DMX run, not terminated; need DMX term kit. | DMX run, not terminated; need DMX term kit. Missing one DMX cable, which is missing? | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-07 | UFMP4 - Semi-Restr Corridor XX03-C028 | Photo |  | 15 | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-S15 | PI1002 - Corridor XX03-C014 | Status | No access | Not installed | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-S15 | PI1002 - Corridor XX03-C014 | Notes | Not reached. | Not installed. - box present | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-S15 | PI1002 - Corridor XX03-C014 | Photo |  | 16 | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-S16 | PI1002 - Corridor XX03-C014 | Status | No access | Not installed | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-S16 | PI1002 - Corridor XX03-C014 | Notes | Not reached. | Not installed. - box present | Field survey | Field update | 5
2026-10-08 | 03 | Devices | 03-S16 | PI1002 - Corridor XX03-C014 | Photo |  | 17 | Field survey | Field update | 5
2026-10-08 | 03 | Punch List | #12 | UFMP4 #1, #2 - Check whether DMX has a through | Tracking status | Open | Closed | Field survey | Field update | 5
2026-10-08 | 03 | Punch List | #12 | UFMP4 #1, #2 - Check whether DMX has a through | Notes | Do they have a through? | Verified only one DMX run to each UFMP8 | Field survey | Field update | 5
2026-10-08 | 03 | Punch List | #26 | PI1002 S15, S16 - Corridor XX03-C014 - Check devices | Tracking status | Open | Closed | Field survey | Field update | 5
2026-10-08 | 03 | Punch List | #26 | PI1002 S15, S16 - Corridor XX03-C014 - Check devices | Notes |  | Updated device list | Field survey | Field update | 5
2026-10-08 | 03 | Photo Log | Photo 15 | UFMP4 #1, #2 | (row added) |  | Both UFMP4s on wall at ceiling; one DMX run to each. | Field survey | Added in the 10/8 survey | 5
2026-10-08 | 03 | Photo Log | Photo 16 | PI1002 S15 - NI | (row added) |  | Box present, no station. | Field survey | Added in the 10/8 survey | 5
2026-10-08 | 03 | Photo Log | Photo 17 | PI1002 S16 - NI | (row added) |  | Box present beside elevator, no station. | Field survey | Added in the 10/8 survey | 5
2026-10-08 | 04 | Devices | 04-03 | CT04LCPB - Elec XX04-1E01 | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-03 | CT04LCPB - Elec XX04-1E01 | Notes | Room locked. | Missing RTO & Jumper, 1 DMX line present, not termed no kit, 0-10 needs termination,( 1 DMX run and 1 net run from lvl 3: net run origin unknown) | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-03 | CT04LCPB - Elec XX04-1E01 | Photo |  | 14 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-04 | EBDK - Elec XX04-1E01 | Status | No access | Installed, untested | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-04 | EBDK - Elec XX04-1E01 | Notes | Room locked. |  | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-04 | EBDK - Elec XX04-1E01 | Photo |  | 14 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-05 | P-NSPS-D-KIT - Elec XX04-1E01 | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-05 | P-NSPS-D-KIT - Elec XX04-1E01 | Notes | Room locked. | 2 nets run into electrical room hanging outside of conduit with 2 "unison" runs (that need to be changed from DMx as already documented) | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-05 | P-NSPS-D-KIT - Elec XX04-1E01 | Photo |  | 14 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-06 | UFMP8 - Conf XX04-3108A/B | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-06 | UFMP8 - Conf XX04-3108A/B | Notes | Room locked. | Installed, no DMX, loads landed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-06 | UFMP8 - Conf XX04-3108A/B | Photo |  | 16 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-07 | UHCI-WM - Conf XX04-3108A/B | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-07 | UHCI-WM - Conf XX04-3108A/B | Notes | Room locked. |  | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S3 | PI1104 - Corridor XX04-C026 | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S3 | PI1104 - Corridor XX04-C026 | Notes | Not reached. | Not Installed - no box. | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S3 | PI1104 - Corridor XX04-C026 | Photo |  | 12 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S15 | PI1004 - Conf XX04-3108B | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S15 | PI1004 - Conf XX04-3108B | Notes | Room locked. | Wire nuts, wrong wire type. | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S16 | PI1004 - Conf XX04-3108A | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-S16 | PI1004 - Conf XX04-3108A | Notes | Room locked. | Wire nuts, wrong wire type. | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D2 | P-DOC-C-LR - Conf XX04-3108B | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D2 | P-DOC-C-LR - Conf XX04-3108B | Notes | Room locked. |  | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D2 | P-DOC-C-LR - Conf XX04-3108B | Photo |  | 15 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D3 | P-DOC-C-LR - Conf XX04-3108A | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D3 | P-DOC-C-LR - Conf XX04-3108A | Notes | Room locked. |  | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D3 | P-DOC-C-LR - Conf XX04-3108A | Photo |  | 15 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D6 | P-DOC-SM2 - Corridor XX04-C023 at Stair D XX04-3S03 | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D6 | P-DOC-SM2 - Corridor XX04-C023 at Stair D XX04-3S03 | Notes | Not reached. | Wire nuts, wrong wire type, no ground (DMX used as ground). Sticky buttons | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D6 | P-DOC-SM2 - Corridor XX04-C023 at Stair D XX04-3S03 | Photo |  | 13 | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D7 | P-LS - Corridor XX04-C028 | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-D7 | P-LS - Corridor XX04-C028 | Notes | Not reached. | Not installed. No ceiling | Field survey | Field update | 6
2026-10-08 | 04 | Devices | 04-08 | Partition sensors - Conf XX04-3108A/B | (row added) |  | Not installed | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Connections | C-03 | CT04LCPA 0-10V Fixtures | To | Control wiring | Fixtures | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-05 | CT04LCPB X DMX to Level 02 | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-05 | CT04LCPB X DMX to Level 02 | Note | Room locked; no term kit | no term kit run to panel | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-06 | CT04LCPB P EBDK panic wire | Status | No access | Installed, untested | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-06 | CT04LCPB P EBDK panic wire | Note | Room locked |  | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-07 | UFMP8 X DMX from Level 06 | To | DMX to Level 06 | DMX from Level 06 | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-07 | UFMP8 X DMX from Level 06 | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-07 | UFMP8 X DMX from Level 06 | Note | Room locked; no term kit | Not run, term kit in box | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-08 | UHCI-WM UV To Level 06 | Status | No access | Not installed | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-08 | UHCI-WM UV To Level 06 | Note | Room locked | Potential Aux 24v hanging outside of conduit in 1E01 next to CT04LCPB. Need to confirm origin | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-09 | Stations & sensors U Devices to P-NSPS-D | Status | No access | Issue | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-09 | Stations & sensors U Devices to P-NSPS-D | Note | P-NSPS-D room locked; # of runs not verified | 2 runs outside conduit; need to be rerun with proper wire (not dmx) | Field survey | Field update | 6
2026-10-08 | 04 | Connections | C-10 | P-NSPS-D N Network to Level 06 | (row added) |  | Issue | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Connections | C-11 | CT04LCPB 0-10V Fixtures | (row added) |  | Issue | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Punch List | #22 | Elec XX04-1E01 - Gain access; survey CT04LCPB, EBDK, P-NSPS-D and Unison terminations | Tracking status | Open | Closed | Field survey | Field update | 6
2026-10-08 | 04 | Punch List | #22 | Elec XX04-1E01 - Gain access; survey CT04LCPB, EBDK, P-NSPS-D and Unison terminations | Notes |  | Updated device list and connections list | Field survey | Field update | 6
2026-10-08 | 04 | Punch List | #23 | Conf XX04-3108A/B - Gain access; survey UFMP8, UHCI-WM, 2x PI1004, 2x P-DOC-C-LR | Tracking status | Open | Closed | Field survey | Field update | 6
2026-10-08 | 04 | Punch List | #23 | Conf XX04-3108A/B - Gain access; survey UFMP8, UHCI-WM, 2x PI1004, 2x P-DOC-C-LR | Notes |  | Updated device list and connections list | Field survey | Field update | 6
2026-10-08 | 04 | Punch List | #24 | PI1104 S3, P-DOC-SM2 D6, P-LS D7 - Check devices | Tracking status | Open | Closed | Field survey | Field update | 6
2026-10-08 | 04 | Punch List | #24 | PI1104 S3, P-DOC-SM2 D6, P-LS D7 - Check devices | Notes |  | Updated in device list | Field survey | Field update | 6
2026-10-08 | 04 | Photo Log | Photo 12 | PI1104 S3 - NI, no box | (row added) |  | Wall at drawn location; no box. | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Photo Log | Photo 13 | P-DOC-SM2 D6 - wire nuts | (row added) |  | Sensor hanging from box; wire nuts on wrong wire type. | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Photo Log | Photo 14 | CT04LCPB, EBDK and P-NSPS-D location | (row added) |  | Panel open; EBDK beside panel; runs hanging outside conduit. | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Photo Log | Photo 15 | P-DOC-C-LR D2, D3 - NI | (row added) |  | Conference room ceiling; no P-DOC-C-LR installed. | Field survey | Added in the 10/8 survey | 6
2026-10-08 | 04 | Photo Log | Photo 16 | UFMP8 - no DMX | (row added) |  | UFMP8 installed above ceiling; loads landed, no DMX. | Field survey | Added in the 10/8 survey | 6
2026-10-09 | B1 | Connections | C-05 | Stations & sensors U Unison to Level B2 ERP | To | Unison | Unison to Level B2 ERP | Ruling | B2 ruling: B1 station Unison lands in the B2 ERP | 2
2026-10-09 | B1 | Connections | C-05 | Stations & sensors U Unison to Level B2 ERP | Note | Run; destination unknown | Lands in B2 ERP; needs to be run down to the NSPS below it | Ruling | B2 ruling: B1 station Unison lands in the B2 ERP | 2
2026-10-09 | B1 | Punch List | #7 | Stations & sensors - Unison runs land in the Level B2 ERP (CTB2LCPB) | Item | Identify destination of Unison runs | Unison runs land in the Level B2 ERP (CTB2LCPB) | Ruling | B2 ruling: B1 station Unison lands in the B2 ERP | 2
2026-10-09 | B1 | Punch List | #7 | Stations & sensors - Unison runs land in the Level B2 ERP (CTB2LCPB) | Notes | Unison run, where does it go? Unison wire on B2 is unlabeled | Need to be run down to the NSPS below it. Unison wire on B2 is unlabeled | Ruling | B2 ruling: B1 station Unison lands in the B2 ERP | 2
2026-10-09 | B2 | Connections | C-02 | CTB2LCPB 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 1
2026-10-09 | B2 | Connections | C-02 | CTB2LCPB 0-10V Fixtures | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 1
2026-10-09 | B2 | Connections | C-04 | 120v Power 120V P-NSPS-D Power Supply | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 1
2026-10-09 | B2 | Connections | C-06 | P-NSPS-D U Unison to Level B1 Devices | Note | Lands in ERP? (Not labled); needs to be run down to the NSPS below it | Lands in ERP? (Not labeled); needs to be run down to the NSPS below it | Correction | Typo | 1
2026-10-09 | B1 | Connections | C-03 | CTB1LCPB 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 2
2026-10-09 | B1 | Connections | C-03 | CTB1LCPB 0-10V Fixtures | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 2
2026-10-09 | 01 | Devices | 01-05 | Equipment Rack 18U - Elec WT01-1E02 | Notes | Missing 1x 1U brush panel, 1x SGM1612 & SGN1021). Run to rack: 3 DMX, 2 net, 1 ground, 1 fiber, 120v run and terminated but box not secured | Missing 1x 1U brush panel, 1x SGM1612 & 1x SGN1021. Run to rack: 3 DMX, 2 net, 1 ground, 1 fiber; 120V run and terminated but box not secured. | Reconcile | 10/8 note in standard wording | 3
2026-10-09 | 01 | Connections | C-03 | CT01LCPB 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 3
2026-10-09 | 01 | Connections | C-07 | CT01LCPA 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 3
2026-10-09 | 01 | Punch List | #53 | All devices - Missing all Device Neuron IDs | # | 38 | 53 | Reconcile | Renumbered; new items added before it | 3
2026-10-09 | 01 | Punch List | #2 | CT01LCPB - Confirm ERP-FT-LVD (0-10V card) is installed | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 3
2026-10-09 | 01 | Punch List | #4 | CT01LCPA - Confirm ERP-FT-LVD (0-10V card) is installed | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 3
2026-10-09 | 01 | Punch List | #6 | EBDK (CT01LCPA) - Check sense feed to EBDK | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 3
2026-10-09 | 01 | Punch List | #7 | Equipment rack - Install 1U brush panel | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 3
2026-10-09 | 01 | Punch List | #8 | Equipment rack - Terminate fiber to Equipment rack Level 06 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 3
2026-10-09 | 01 | Punch List | #8 | Equipment rack - Terminate fiber to Equipment rack Level 06 | Notes | Fiber terminated in equipment rack; Missing kit parts SGN1021, N2019 (SFP) | Fiber terminated in equipment rack; missing kit parts SGM1612, SGN1021 | Ruling | Per Landry: only SGM1612 and SGN1021 still missing | 3
2026-10-09 | 01 | Punch List | #9 | Equipment rack - Survey outgoing runs (DMX x4, network x2, fiber, NG) and check Unison wiring at each device | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 3
2026-10-09 | 01 | Punch List | #36 | PI1002 S21 - Passage XX01-C005A - Check device | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 3
2026-10-09 | 01 | Punch List | #37 | PI1004 S18, PI1104 S20 - Check devices | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #2 | CT01LCPB, CT01LCPA - ERP-FT-LVD (0-10V card) | Source | Punch #2, #4 | Punch #38, #39 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #2 | CT01LCPB, CT01LCPA - ERP-FT-LVD (0-10V card) | Notes | MSS 10/1 shows installed; confirm on site | Need to be ordered | Reconcile | LVD confirmed missing in the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #4 | Equipment rack - Fiber kit part | Part status | Needed | Installed | Ruling | Per Landry: only SGM1612 and SGN1021 still missing | 3
2026-10-09 | 01 | Missing Parts | #4 | Equipment rack - Fiber kit part | Notes | Need to be ordered | Verified 10/8 | Ruling | Per Landry: only SGM1612 and SGN1021 still missing | 3
2026-10-09 | 01 | Missing Parts | #5 | Equipment rack - Fiber kit part | Part status | Needed | Installed | Ruling | Per Landry: only SGM1612 and SGN1021 still missing | 3
2026-10-09 | 01 | Missing Parts | #5 | Equipment rack - Fiber kit part | Notes | Need to be ordered | Verified 10/8 | Ruling | Per Landry: only SGM1612 and SGN1021 still missing | 3
2026-10-09 | 01 | Missing Parts | #8 | Equipment rack - DMX termination kit - B3A Canyon run | Source | Punch #9 | Punch #42 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #9 | Equipment rack - DMX termination kit - C13A Oculus run | Source | Punch #9 | Punch #43 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #10 | Equipment rack - DMX termination kit - D1 ED Column Capital run | Source | Punch #9 | Punch #44 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #11 | Equipment rack - DMX termination kit - UFMP4 run | Source | Punch #9 | Punch #45 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #16 | S5, S7-S14, S20, S22 - PI1104 station | Device / Location | S5, S7-S14, S22 | S5, S7-S14, S20, S22 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #16 | S5, S7-S14, S20, S22 - PI1104 station | Qty | 10 | 11 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #16 | S5, S7-S14, S20, S22 - PI1104 station | Source | Punch #22-28, #30, #31, #33 | Punch #22-28, #30, #31, #33, #52 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #17 | S16, S18 - PI1004 station | Device / Location | S16 | S16, S18 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #17 | S16, S18 - PI1004 station | Qty | 1 | 2 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 01 | Missing Parts | #17 | S16, S18 - PI1004 station | Source | Punch #32 | Punch #32, #51 | Reconcile | Updated for items added after the 10/8 survey | 3
2026-10-09 | 02 | Devices | 02-03 | P-NSPS-D-KIT - Elec XX02-1E01 | Notes | Not Installed. No unison wire in Elec XX-2-1E01 | Not Installed. No Unison wire in Elec XX02-1E01. | Correction | Typo | 4
2026-10-09 | 02 | Connections | C-03 | CT02LCPA 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 4
2026-10-09 | 02 | Connections | C-03 | CT02LCPA 0-10V Fixtures | Note | Not landed | Run, not terminated | Reconcile | Standard wording | 4
2026-10-09 | 02 | Connections | C-07 | CT02LCPB 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 4
2026-10-09 | 02 | Connections | C-09 | Stations & sensors U Devices to P-NSPS-D | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 4
2026-10-09 | 02 | Punch List | #32 | All devices - Missing all Device Neuron IDs | # | 29 | 32 | Reconcile | Renumbered; new items added before it | 4
2026-10-09 | 02 | Punch List | #2 | CT02LCPA - Check (2) 0-10V headers | Photo | 5 | 6 | Correction | Photo 5 is CT02LCPB; CT02LCPA is photo 6 | 4
2026-10-09 | 02 | Punch List | #2 | CT02LCPA - Check (2) 0-10V headers | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 4
2026-10-09 | 02 | Punch List | #4 | CT02LCPA - Terminate DMX to Level 03 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 4
2026-10-09 | 02 | Punch List | #5 | CT02LCPA - Terminate DMX to Level 01 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 4
2026-10-09 | 02 | Punch List | #7 | P-NSPS-D - Elec XX02-1E01 - Not installed: install P-NSPS-D and land 120V and Unison wire | Notes |  | Unison wire location not found | Reconcile | Note added from the 10/8 survey | 4
2026-10-09 | 02 | Punch List | #9 | CT02LCPB - Terminate DMX to Level 03 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 4
2026-10-09 | 02 | Punch List | #10 | CT02LCPB - Terminate DMX to UFMP4 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 4
2026-10-09 | 02 | Punch List | #11 | EBDK (CT02LCPB) - Provide sense feed to EBDK | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 4
2026-10-09 | 02 | Punch List | #27 | PI1002 S11 - Elevator Lobby A XX02-C001 - Check device | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 4
2026-10-09 | 02 | Punch List | #28 | PI1002 S15 - East corridor south of Seating - Check device | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 4
2026-10-09 | 02 | Punch List | #8 | CT02LCPB - Run and land 0-10V control wiring | Item | Land 0-10V control wiring | Run and land 0-10V control wiring | Reconcile | 0-10V not run, so the item is run and land | 4
2026-10-09 | 02 | Punch List | #8 | CT02LCPB - Run and land 0-10V control wiring | Type | Termination | Cable not run | Reconcile | 0-10V not run, so the item is run and land | 4
2026-10-09 | 02 | Missing Parts | #7 | S1, S5, S11, S13, S14, S15 - PI1002 station | Device / Location | S1, S5, S13, S14 | S1, S5, S11, S13, S14, S15 | Reconcile | Updated for items added after the 10/8 survey | 4
2026-10-09 | 02 | Missing Parts | #7 | S1, S5, S11, S13, S14, S15 - PI1002 station | Qty | 4 | 6 | Reconcile | Updated for items added after the 10/8 survey | 4
2026-10-09 | 02 | Missing Parts | #7 | S1, S5, S11, S13, S14, S15 - PI1002 station | Source | Punch #15, #16, #18, #19 | Punch #15, #16, #18, #19, #30, #31 | Reconcile | Updated for items added after the 10/8 survey | 4
2026-10-09 | 03 | Devices | 03-S15 | PI1002 - Corridor XX03-C014 | Notes | Not installed. - box present | Not Installed - box present. | Reconcile | 10/8 note in standard wording | 5
2026-10-09 | 03 | Devices | 03-S16 | PI1002 - Corridor XX03-C014 | Notes | Not installed. - box present | Not Installed - box present. | Reconcile | 10/8 note in standard wording | 5
2026-10-09 | 03 | Connections | C-03 | CT03LCPA 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 5
2026-10-09 | 03 | Connections | C-08 | CT03LCPB 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 5
2026-10-09 | 03 | Punch List | #31 | All devices - Missing all Device Neuron IDs | # | 27 | 31 | Reconcile | Renumbered; new items added before it | 5
2026-10-09 | 03 | Punch List | #3 | CT03LCPA - Terminate DMX to Level 04 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 5
2026-10-09 | 03 | Punch List | #4 | CT03LCPA - Terminate DMX to Level 02 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 5
2026-10-09 | 03 | Punch List | #7 | CT03LCPB - Terminate DMX to Level 04 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 5
2026-10-09 | 03 | Punch List | #8 | CT03LCPB - Terminate DMX to Level 02 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 5
2026-10-09 | 03 | Punch List | #10 | UFMP4 #1 - Semi-Restr Corridor XX03-C028 - Terminate DMX | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 5
2026-10-09 | 03 | Punch List | #11 | UFMP4 #2 - Semi-Restr Corridor XX03-C028 - Terminate DMX | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 5
2026-10-09 | 03 | Punch List | #12 | UFMP4 #1, #2 - Check whether DMX has a through | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 5
2026-10-09 | 03 | Punch List | #12 | UFMP4 #1, #2 - Check whether DMX has a through | Notes | Verified only one DMX run to each UFMP8 | Verified only one DMX run to each UFMP4 | Correction | Typo | 5
2026-10-09 | 03 | Punch List | #26 | PI1002 S15, S16 - Corridor XX03-C014 - Check devices | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 5
2026-10-09 | 03 | Missing Parts | #12 | S11, S12, S13, S15, S16, S18 - PI1002 station | Device / Location | S11, S12, S13, S18 | S11, S12, S13, S15, S16, S18 | Reconcile | Updated for items added after the 10/8 survey | 5
2026-10-09 | 03 | Missing Parts | #12 | S11, S12, S13, S15, S16, S18 - PI1002 station | Qty | 4 | 6 | Reconcile | Updated for items added after the 10/8 survey | 5
2026-10-09 | 03 | Missing Parts | #12 | S11, S12, S13, S15, S16, S18 - PI1002 station | Source | Punch #18-21 | Punch #18-21, #29, #30 | Reconcile | Updated for items added after the 10/8 survey | 5
2026-10-09 | 04 | Devices | 04-03 | CT04LCPB - Elec XX04-1E01 | Notes | Missing RTO & Jumper, 1 DMX line present, not termed no kit, 0-10 needs termination,( 1 DMX run and 1 net run from lvl 3: net run origin unknown) | Missing ERP-RTO card + jumper. 1 DMX run from Level 03, not terminated; no term kit. 0-10V not landed. 1 network run from Level 03, origin unknown. | Reconcile | 10/8 note in standard wording | 6
2026-10-09 | 04 | Devices | 04-05 | P-NSPS-D-KIT - Elec XX04-1E01 | Notes | 2 nets run into electrical room hanging outside of conduit with 2 "unison" runs (that need to be changed from DMx as already documented) | Not Installed. 2 network runs and 2 Unison runs hanging outside conduit in the electrical room; Unison runs are DMX cable and need to be re-pulled. | Reconcile | 10/8 note in standard wording | 6
2026-10-09 | 04 | Devices | 04-07 | UHCI-WM - Conf XX04-3108A/B | Notes |  | Not Installed. | Reconcile | 10/8 note in standard wording | 6
2026-10-09 | 04 | Devices | 04-D2 | P-DOC-C-LR - Conf XX04-3108B | Notes |  | Not Installed. | Reconcile | 10/8 note in standard wording | 6
2026-10-09 | 04 | Devices | 04-D3 | P-DOC-C-LR - Conf XX04-3108A | Notes |  | Not Installed. | Reconcile | 10/8 note in standard wording | 6
2026-10-09 | 04 | Devices | 04-D7 | P-LS - Corridor XX04-C028 | Notes | Not installed. No ceiling | Not Installed - no ceiling. | Reconcile | 10/8 note in standard wording | 6
2026-10-09 | 04 | Connections | C-01 | CT04LCPA X DMX to Level 06 | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 6
2026-10-09 | 04 | Connections | C-05 | CT04LCPB X DMX to Level 03 UFMP4 | To | DMX to Level 02 | DMX to Level 03 UFMP4 | Ruling | Per Landry: cable should come from the Level 03 UFMP4 | 6
2026-10-09 | 04 | Connections | C-05 | CT04LCPB X DMX to Level 03 UFMP4 | Note | no term kit run to panel | Run, not terminated; no term kit | Reconcile | Standard wording | 6
2026-10-09 | 04 | Punch List | #44 | All devices - Missing all Device Neuron IDs | # | 25 | 44 | Reconcile | Renumbered; new items added before it | 6
2026-10-09 | 04 | Punch List | #44 | All devices - Missing all Device Neuron IDs | Device | Missing all Device Neuron IDs | All devices | Correction | Neuron ID item in standard format | 6
2026-10-09 | 04 | Punch List | #44 | All devices - Missing all Device Neuron IDs | Item |  | Missing all Device Neuron IDs | Correction | Neuron ID item in standard format | 6
2026-10-09 | 04 | Punch List | #4 | CT04LCPA - Terminate DMX to Level 06 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 6
2026-10-09 | 04 | Punch List | #5 | CT04LCPA - Terminate DMX to Level 03 | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 6
2026-10-09 | 04 | Punch List | #22 | Elec XX04-1E01 - Gain access; survey CT04LCPB, EBDK, P-NSPS-D and Unison terminations | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 6
2026-10-09 | 04 | Punch List | #23 | Conf XX04-3108A/B - Gain access; survey UFMP8, UHCI-WM, 2x PI1004, 2x P-DOC-C-LR | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 6
2026-10-09 | 04 | Punch List | #24 | PI1104 S3, P-DOC-SM2 D6, P-LS D7 - Check devices | Date closed |  | 2026-10-08 | Reconcile | Closed in the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #1 | CT04LCPA, CT04LCPB - ERP-RTO card + jumper | Device / Location | CT04LCPA | CT04LCPA, CT04LCPB | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #1 | CT04LCPA, CT04LCPB - ERP-RTO card + jumper | Qty | 1 | 2 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #1 | CT04LCPA, CT04LCPB - ERP-RTO card + jumper | Source | Punch #1 | Punch #1, #25 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #4 | CT04LCPB - DMX termination kit - Level 03 UFMP4 run | Part | DMX termination kit - Level 02 run | DMX termination kit - Level 03 UFMP4 run | Ruling | Per Landry: cable should come from the Level 03 UFMP4 | 6
2026-10-09 | 04 | Missing Parts | #4 | CT04LCPB - DMX termination kit - Level 03 UFMP4 run | Source | Device level; room locked | Punch #27 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #5 | UFMP8 - DMX termination kit - Level 06 run | Source | Device level; room locked | Punch #32 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #5 | UFMP8 - DMX termination kit - Level 06 run | Part status | Needed | On site | Reconcile | Term kit in box (10/8) | 6
2026-10-09 | 04 | Missing Parts | #5 | UFMP8 - DMX termination kit - Level 06 run | Notes | Need to be ordered | Term kit in box | Reconcile | Term kit in box (10/8) | 6
2026-10-09 | 04 | Missing Parts | #6 | S3, S4, S12 - Backbox for station | Device / Location | S4, S12 | S3, S4, S12 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #6 | S3, S4, S12 - Backbox for station | Qty | 2 | 3 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #6 | S3, S4, S12 - Backbox for station | Source | Punch #15, #18 | Punch #15, #18, #36 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #7 | S3, S4 - PI1104 station | Device / Location | S4 | S3, S4 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #7 | S3, S4 - PI1104 station | Qty | 1 | 2 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #7 | S3, S4 - PI1104 station | Source | Punch #15 | Punch #15, #36 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #9 | D1, D2, D3, D4 - P-DOC-C-LR sensor | Device / Location | D1, D4 | D1, D2, D3, D4 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #9 | D1, D2, D3, D4 - P-DOC-C-LR sensor | Qty | 2 | 4 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 04 | Missing Parts | #9 | D1, D2, D3, D4 - P-DOC-C-LR sensor | Source | Punch #20, #21 | Punch #20, #21, #39, #40 | Reconcile | Updated for items added after the 10/8 survey | 6
2026-10-09 | 06 | Punch List | #17 | All devices - Missing all Device Neuron IDs | Device | Missing all Device Neuron IDs | All devices | Correction | Neuron ID item in standard format | 7
2026-10-09 | 06 | Punch List | #17 | All devices - Missing all Device Neuron IDs | Item |  | Missing all Device Neuron IDs | Correction | Neuron ID item in standard format | 7
2026-10-09 | 06M | Connections | C-01 | Equipment rack X DMX to B3B Elev Core C fixture | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 8
2026-10-09 | 06M | Connections | C-02 | Equipment rack X DMX to B7 Stair A fixture | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 8
2026-10-09 | 06M | Connections | C-03 | Equipment rack X Spare DMX out | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 8
2026-10-09 | 06M | Connections | C-05 | Equipment rack F Equipment rack Level 28 | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 8
2026-10-09 | 06M | Connections | C-07 | CT06LCPB X DMX out | Status | Issue | Not installed | Ruling | A cable that is not pulled is Not installed | 8
2026-10-09 | 06M | Connections | C-11 | CT06LCPB 0-10V Fixtures | To | Control wiring | Fixtures | Ruling | 0-10V rows read Fixtures | 8
2026-10-09 | 06M | Punch List | #3 | Equipment rack - Install 1U brush panel | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 8
2026-10-09 | 06M | Punch List | #12 | CT06LCPA - Terminate DMX | Owner | ETC/EC | EC/ETC | Ruling | Joint owner label is EC/ETC | 8
2026-10-09 | 06M | Punch List | #15 | PI1002 stations - Terminate Unison runs at rack | Level | 06/06M | 06M | Ruling | Rack Unison item belongs to 06M | 8
2026-10-09 | 06M | Missing Parts | #11 | CT06LCPB - DMX termination kit - 6M Equipment Rack run | Level |  | 06M | Correction | Level was blank | 8
2026-10-09 | 06M | Missing Parts | #13 | CT06LCPA - DMX termination kit - Level 04 run | Level |  | 06M | Correction | Level was blank | 8
2026-10-09 | B2 | Connections | C-01 | CTB2LCPB X DMX to Level B1 CTB1LCPB | To | DMX to Level 01 | DMX to Level B1 CTB1LCPB | Riser cross-check | To field follows the riser | 1
2026-10-09 | B2 | Connections | C-01 | CTB2LCPB X DMX to Level B1 CTB1LCPB | Note | Run, not terminated; no term kit | Run, not terminated; no term kit. Survey drawing showed Level 01 | Riser cross-check | Note keeps the surveyed destination or a possible alternate | 1
2026-10-09 | B2 | Punch List | #2 | CTB2LCPB - Terminate DMX to Level B1 | Item | Terminate DMX to Level 01 | Terminate DMX to Level B1 | Riser cross-check | Renamed to match the riser destination | 1
2026-10-09 | B2 | Missing Parts | #1 | CTB2LCPB - DMX termination kit - Level B1 run | Part | DMX termination kit - Level 01 run | DMX termination kit - Level B1 run | Riser cross-check | Renamed to match the riser destination | 1
2026-10-09 | 01 | Connections | C-01 | CT01LCPB X DMX to Level 02 UFMP4 | To | DMX to Level 02 | DMX to Level 02 UFMP4 | Riser cross-check | To field follows the riser | 3
2026-10-09 | 01 | Punch List | #46 | Equipment rack - Identify unidentified DMX wire at rack | Notes | One of the four outgoing DMX runs? | One of the four outgoing DMX runs? Riser: likely the Level B1 run | Riser cross-check | Riser note added | 3
2026-10-09 | 02 | Connections | C-10 | P-NSPS-D N Network to Level 01 equipment rack | From | CT02LCPB | P-NSPS-D | Riser cross-check | Riser lands this run at the P-NSPS-D | 4
2026-10-09 | 02 | Connections | C-10 | P-NSPS-D N Network to Level 01 equipment rack | To | Network from Level 01 | Network to Level 01 equipment rack | Riser cross-check | To field follows the riser | 4
2026-10-09 | 02 | Connections | C-10 | P-NSPS-D N Network to Level 01 equipment rack | Note | Run; purpose unknown | Run found at CT02LCPB in Elec XX02-1E02; riser lands it at the P-NSPS-D in Elec XX02-1E01 | Riser cross-check | Note keeps the surveyed destination or a possible alternate | 4
2026-10-09 | 02 | Punch List | #29 | CT02LCPB - Identify purpose of network run from Level 01 | Notes | 1 net run from Level 01; for what? | 1 net run from Level 01; for what? Riser: network for the P-NSPS-D in Elec XX02-1E01 | Riser cross-check | Riser note added | 4
2026-10-09 | 03 | Connections | C-01 | CT03LCPA X DMX to UFMP4s | To | DMX to Level 04 | DMX to UFMP4s | Riser cross-check | To field follows the riser | 5
2026-10-09 | 03 | Connections | C-01 | CT03LCPA X DMX to UFMP4s | Note | Run, not terminated; no term kit | Run, not terminated; no term kit. Survey drawing showed Level 04 | Riser cross-check | Note keeps the surveyed destination or a possible alternate | 5
2026-10-09 | 03 | Connections | C-05 | CT03LCPA N Network | Note | Run; destination unknown | Run; destination unknown. One may be the P-NSPS-D network to Level 06? | Riser cross-check | Note keeps the surveyed destination or a possible alternate | 5
2026-10-09 | 03 | Connections | C-10 | UFMP4 #1, #2 X DMX to Level 04 CT04LCPA | To | DMX to Level 06 | DMX to Level 04 CT04LCPA | Riser cross-check | To field follows the riser | 5
2026-10-09 | 03 | Connections | C-10 | UFMP4 #1, #2 X DMX to Level 04 CT04LCPA | Qty | 2 | 1 | Riser cross-check | One run to Level 04 on the riser | 5
2026-10-09 | 03 | Connections | C-10 | UFMP4 #1, #2 X DMX to Level 04 CT04LCPA | Note | Run, not terminated; no term kit | Run, not terminated; no term kit. Survey drawing showed Level 06 (2 runs) | Riser cross-check | Note keeps the surveyed destination or a possible alternate | 5
2026-10-09 | 03 | Connections | C-13 | UFMP4 #1, #2 X Missing DMX run (one per UFMP4) | Note | Not run; which is missing? Level 04 CT04LCPB DMX should come from a Level 03 UFMP4 | Not run; which is missing? Level 04 CT04LCPB DMX may come from a Level 03 UFMP4? Riser: missing run may be the link between UFMP4 #1 and #2? | Riser cross-check | Riser note added | 5
2026-10-09 | 03 | Punch List | #5 | CT03LCPA - Identify purpose of 2 network runs | Notes | 2 nets run, where do they go? | 2 nets run, where do they go? One may be the P-NSPS-D network to Level 06? | Riser cross-check | Riser note added | 5
2026-10-09 | 03 | Punch List | #3 | CT03LCPA - Terminate DMX to UFMP4s | Item | Terminate DMX to Level 04 | Terminate DMX to UFMP4s | Riser cross-check | Renamed to match the riser destination | 5
2026-10-09 | 03 | Missing Parts | #2 | CT03LCPA - DMX termination kit - UFMP4 run | Part | DMX termination kit - Level 04 run | DMX termination kit - UFMP4 run | Riser cross-check | Renamed to match the riser destination | 5
2026-10-09 | 03 | Missing Parts | #6 | UFMP4 #1 - DMX termination kit - CT03LCPA or Level 04 run | Part | DMX termination kit - Level 06 run | DMX termination kit - CT03LCPA or Level 04 run | Riser cross-check | Renamed to match the riser destination | 5
2026-10-09 | 03 | Missing Parts | #7 | UFMP4 #2 - DMX termination kit - CT03LCPA or Level 04 run | Part | DMX termination kit - Level 06 run | DMX termination kit - CT03LCPA or Level 04 run | Riser cross-check | Renamed to match the riser destination | 5
2026-10-09 | 04 | Connections | C-02 | CT04LCPA X DMX to Level 03 UFMP4s | To | DMX to Level 03 | DMX to Level 03 UFMP4s | Riser cross-check | To field follows the riser | 6
2026-10-09 | 04 | Connections | C-05 | CT04LCPB X DMX to Level 03 CT03LCPB | To | DMX to Level 03 UFMP4 | DMX to Level 03 CT03LCPB | Riser cross-check | To field follows the riser | 6
2026-10-09 | 04 | Connections | C-05 | CT04LCPB X DMX to Level 03 CT03LCPB | Note | Run, not terminated; no term kit | Run, not terminated; no term kit. May come from the Level 03 UFMP4? | Riser cross-check | Note keeps the surveyed destination or a possible alternate | 6
2026-10-09 | 04 | Connections | C-12 | CT04LCPB N Network from Level 03 | Note | Run; origin unknown | Run; origin unknown. Not on riser; may be the Level 03 P-NSPS-D network to Level 06 passing through? | Riser cross-check | Not on the riser; possible source noted | 6
2026-10-09 | 04 | Punch List | #27 | CT04LCPB - Terminate DMX to Level 03 | Item | Terminate DMX to Level 03 UFMP4 | Terminate DMX to Level 03 | Riser cross-check | Renamed to match the riser destination | 6
2026-10-09 | 04 | Missing Parts | #4 | CT04LCPB - DMX termination kit - Level 03 run | Part | DMX termination kit - Level 03 UFMP4 run | DMX termination kit - Level 03 run | Riser cross-check | Renamed to match the riser destination | 6
2026-10-09 | 06M | Connections | C-07 | CT06LCPB X DMX to Level 09 | To | DMX out | DMX to Level 09 | Riser cross-check | To field follows the riser | 8
2026-10-09 | 06M | Connections | C-07 | CT06LCPB X DMX to Level 09 | Qty | 2 | 1 | Riser cross-check | Split into one row per cable | 8
2026-10-09 | 06M | Connections | C-09 | CT06LCPA X DMX to Level 09 | To | DMX in/out | DMX to Level 09 | Riser cross-check | To field follows the riser | 8
2026-10-09 | 06M | Connections | C-09 | CT06LCPA X DMX to Level 09 | Qty | 2 | 1 | Riser cross-check | Split into one row per cable | 8
2026-10-09 | 06M | Connections | C-09 | CT06LCPA X DMX to Level 09 | Note | Only one run pulled; no term kits | Only one of the two CT06LCPA runs pulled, which one undetermined; no term kit | Riser cross-check | Reworded for the split into one row per cable | 8
2026-10-09 | 01 | Devices | 01-07 | UFMP4 - Vest WT01-1044 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-07 | UFMP4 - Vest WT01-1044 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-08 | UFMP4 - BH OBS RM 47 WT01-2027 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-08 | UFMP4 - BH OBS RM 47 WT01-2027 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-09 | UFMP4 - BH OBS RM 48 WT01-2010 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-09 | UFMP4 - BH OBS RM 48 WT01-2010 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-10 | UFMP4 - BH OBS RM 49 WT01-2008 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-10 | UFMP4 - BH OBS RM 49 WT01-2008 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-11 | UFMP4 - BH OBS RM 50 WT01-2006 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-11 | UFMP4 - BH OBS RM 50 WT01-2006 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-12 | UFMP4 - BH OBS RM 51 WT01-2004 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-12 | UFMP4 - BH OBS RM 51 WT01-2004 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-13 | UFMP4 - BH OBS RM 52 WT01-2002 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-13 | UFMP4 - BH OBS RM 52 WT01-2002 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 3
2026-10-09 | 01 | Devices | 01-S6 | PI1002 - Humidifier Closet WT01-2033 | Notes | Blocked | Blocked by Walter Tower barricade. | Master edit | Landry's edit in the master | 3
2026-10-09 | 02 | Devices | 02-06 | UFMP4 - Elec XX02-1E02 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 4
2026-10-09 | 02 | Devices | 02-06 | UFMP4 - Elec XX02-1E02 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 4
2026-10-09 | 03 | Devices | 03-06 | UFMP4 - Semi-Restr Corridor XX03-C028 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 5
2026-10-09 | 03 | Devices | 03-06 | UFMP4 - Semi-Restr Corridor XX03-C028 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 5
2026-10-09 | 03 | Devices | 03-07 | UFMP4 - Semi-Restr Corridor XX03-C028 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 5
2026-10-09 | 03 | Devices | 03-07 | UFMP4 - Semi-Restr Corridor XX03-C028 | Type | Foundry 4-circuit module | Foundry 4-circuit panel | Master edit | Landry's edit in the master | 5
2026-10-09 | 04 | Devices | 04-06 | UFMP8 - Conf XX04-3108A/B | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 6
2026-10-09 | 04 | Devices | 04-06 | UFMP8 - Conf XX04-3108A/B | Type | Foundry 8-circuit module | Foundry 8-circuit panel | Master edit | Landry's edit in the master | 6
2026-10-09 | 06M | Devices | 06M-04 | CT06LCPA - Near Elevator Machine Room XX06M-1EM02 | Category | Foundry module | Foundry panel | Master edit | Landry's edit in the master | 8
2026-10-09 | 03 | Connections | C-11 | 120v Power 120V P-NSPS-D Power Supply | From | P-NSPS-D | 120v Power | Ruling | 120V never comes from the NSPS; the NSPS needs 120V | 5
2026-10-09 | 03 | Connections | C-11 | 120v Power 120V P-NSPS-D Power Supply | To | Power 120v | P-NSPS-D Power Supply | Ruling | 120V never comes from the NSPS; the NSPS needs 120V | 5
2026-10-09 | 06M | Connections | C-20 | Equipment rack N Network to Level 09 | Status | No access | Not started | Ruling | Per Landry: floors above 06M are not started | 8
2026-10-09 | 06M | Connections | C-21 | Equipment rack N Network to Level 10 | Status | No access | Not started | Ruling | Per Landry: floors above 06M are not started | 8
2026-10-09 | 06M | Connections | C-22 | Equipment rack N Network to Level 11 | Status | No access | Not started | Ruling | Per Landry: floors above 06M are not started | 8
2026-10-09 | 06M | Connections | C-23 | Equipment rack X DMX to Level 11 | Status | No access | Not started | Ruling | Per Landry: floors above 06M are not started | 8
2026-10-09 | 06M | Connections | C-24 | Equipment rack N Network to Level 12 | Status | No access | Not started | Ruling | Per Landry: floors above 06M are not started | 8
2026-10-09 | 06 | Punch List | #18 | All devices - Missing all Device Neuron IDs | # | 17 | 18 | Reconcile | Renumbered; new item added before it | 7

## Lists (hidden)
Device status | Tracking status | Part status | Connection status
Complete | Open | Needed | Complete
Installed, untested | In progress | Ordered | Installed, untested
Issue | Closed | On site | Issue
Not installed |  | Installed | Not installed
No access |  |  | No access
Not started